ELC4340_Spring13_HW6.doc, Due Tuesday, March 5, 2013 

SUMMARY OF Positive/Negative Sequence HAND Calculations

Assumptions

Balanced, far from ground, ground wires ignored.  Valid for identical single conductors per phase, or for identical symmetric phase bundles with N conductors per phase and bundle radius A.

Computation of positive/negative sequence capacitance


[image: image41.emf] 

R   jωL  

jωC/2  

1  

jωC/2  

1   +   200kVrms   −  

400Ω  

P 1  + jQ 1          I 1  

Q C1   produced  

P 2  + jQ 2          I 2  

Q L   absorbed  

Q C2   produced  

+   V R   /  δ R   −  

One circuit of the 345kV line geometry, 100km long  

 farads per meter,

where


[image: image2.wmf]3

/

bc

ac

ab

D

D

D

GMD

·

·

=

-

+

 meters,

where 
[image: image3.wmf]bc

ac

ab

D

D

D

,

,

 are

· distances between phase conductors if the line has one conductor per phase, or

· distances between phase bundle centers if the line has symmetric phase bundles,

and where

· 
[image: image4.wmf]-

+

/

C

GMR

 is the actual conductor radius r (in meters) if the line has one conductor per phase, or

· 
[image: image5.wmf]N

N

C

A

r

N

GMR

1

/

-

-

+

·

·

=

if the line has symmetric phase bundles.

Computation of positive/negative sequence inductance


[image: image6.wmf]-

+

-

+

-

+

=

/

/

/

ln

2

L

o

GMR

GMD

L

p

m

 henrys per meter,

where 
[image: image7.wmf]-

+

/

GMD

 is the same as for capacitance, and

· for the single conductor case, 
[image: image8.wmf]-

+

/

L

GMR

 is the conductor 
[image: image9.wmf]gmr

r

 (in meters), which takes into account both stranding and the 
[image: image10.wmf]4

/

1

-

e

 adjustment for internal inductance.  If 
[image: image11.wmf]gmr

r

 is not given, then assume 
[image: image12.wmf]4

/

1

-

=

re

r

gmr

, and

· for bundled conductors, 
[image: image13.wmf]N

N

gmr

L

A

r

N

GMR

1

/

-

-

+

·

·

=

if the line has symmetric phase bundles.

Computation of positive/negative sequence resistance

R is the 60Hz resistance of one conductor if the line has one conductor per phase.  If the line has symmetric phase bundles, then divide the one-conductor resistance by N.

Some commonly-used symmetric phase bundle configurations

[image: image1.wmf]-

+

-

+

-

+

=

/

/

/

ln

2

C

o

GMR

GMD

C

pe


SUMMARY OF ZERO SEQUENCE HAND CALCULATIONS

Assumptions

Ground wires are ignored.  The a-b-c phases are treated as one bundle.  If individual phase conductors are bundled, they are treated as single conductors using the bundle radius method.  For capacitance, the Earth is treated as a perfect conductor.  For inductance and resistance, the Earth is assumed to have uniform resistivity 
[image: image14.wmf]r

.  Conductor sag is taken into consideration, and a good assumption for doing this is to use an average conductor height equal to (1/3 the conductor height above ground at the tower, plus 2/3 the conductor height above ground at the maximum sag point).

The zero sequence excitation mode is shown below, along with an illustration of the relationship between bundle C and L and zero sequence C and L.  Since the bundle current is actually 3Io, the zero sequence resistance and inductance are three times that of the bundle, and the zero sequence capacitance is one-third that of the bundle.


Computation of zero sequence capacitance


[image: image15.wmf]0

0

0

ln

2

3

1

C

C

o

GMR

GMD

C

pe

·

=

 farads per meter,

where 
[image: image16.wmf]0

C

GMD

 is the average height (with sag factored in) of the a-b-c bundle above perfect Earth.  
[image: image17.wmf]0

C

GMD

 is computed using 


[image: image18.wmf]9

2

2

2

0

i

bc

i

ac

i

ab

i

cc

i

bb

i

aa

C

D

D

D

D

D

D

GMD

·

·

·

·

·

=

 meters,

where 
[image: image19.wmf]i

aa

D

 is the distance from a to a-image, 
[image: image20.wmf]i

ab

D

 is the distance from a to b-image, and so forth.  The Earth is assumed to be a perfect conductor, so that the images are the same distance below the Earth as are the conductors above the Earth.  Also,


[image: image21.wmf]9

2

2

2

3

/

0

bc

ac

ab

C

C

D

D

D

GMR

GMR

·

·

·

=

-

+

 meters,

where 
[image: image22.wmf]-

+

/

C

GMR

, 
[image: image23.wmf]ab

D

, 
[image: image24.wmf]ac

D

, and 
[image: image25.wmf]bc

D

 were described previously.

Computation of zero sequence inductance


[image: image26.wmf]0

0

ln

2

3

L

o

GMR

L

d

p

m

·

=

 Henrys per meter, 
[image: image27.wmf]0

C

GMD

³

d


where skin depth 
[image: image28.wmf]f

o

pm

r

d

2

=

 meters.  Resistivity ρ = 100 ohm-meter is commonly used.  For poor soils, ρ = 1000 ohm-meter is commonly used.  For 60 Hz, and ρ = 100 ohm-meter, skin depth δ is 459 meters.  To cover situations with low resistivity, use 
[image: image29.wmf]0

C

GMD

 (from the previous page) as a lower limit for δ
The geometric mean bundle radius is computed using


[image: image30.wmf]9

2

2

2

3

/

0

bc

ac

ab

L

L

D

D

D

GMR

GMR

·

·

·

=

-

+

 meters,

where 
[image: image31.wmf]-

+

/

L

GMR

, 
[image: image32.wmf]ab

D

, 
[image: image33.wmf]ac

D

, and 
[image: image34.wmf]bc

D

 were shown previously.

Computation of zero sequence resistance

There are two components of zero sequence line resistance.  First, the equivalent conductor resistance is the 60Hz resistance of one conductor if the line has one conductor per phase.  If the line has symmetric phase bundles with N conductors per bundle, then divide the one-conductor resistance by N.

Second, the effect of resistive earth is included by adding the following term to the conductor resistance:


[image: image35.wmf]f

7

10

869

.

9

3

-

·

·

 ohms per meter (see Bergen),

where the multiplier of three is needed to take into account the fact that all three zero sequence currents flow through the Earth.

As a general rule, 
· 
[image: image36.wmf]-

+

/

C

 usually works out to be about 12 picoF per meter, 
· 
[image: image37.wmf]-

+

/

L

 works out to be about 1 microH per meter (including internal inductance).  
· 
[image: image38.wmf]0

C

 is usually about 6 picoF per meter.  
· 
[image: image39.wmf]0

L

 is usually about 2 microH per meter if the line has ground wires and typical Earth resistivity, or about 3 microH per meter for lines without ground wires or poor earth resistivity.

The velocity of propagation, 
[image: image40.wmf]LC

1

, is approximately the speed of light (3 x 108 m/s) for positive and negative sequences, and about 0.8 times that for zero sequence.


The HW#6 Problem.
Use the left-hand circuit of the 345kV line geometry given two pages back.  Determine the L, C, R line parameters, per unit length, for positive/negative and zero sequence.

Now, focus on a balanced three-phase case, where only positive sequence is important, and work the following problem using your L, C, R positive sequence line parameters:

For a 200km long segment, determine the P’s, Q’s, I’s, VR, and δR for switch open and switch closed cases.  The generator voltage phase angle is zero. 


A





A





A





N = 2





N = 3





N = 4





+


Vo


–





Io →





Io →





Io →





3Io →





Cbundle





+


Vo


–





Io →





Io →





Io →





3Io →





3Io ↓





Lbundle





+


Vo


–





Io →





Io →





Io →





3Io →





Co





Co





Co





Io →





+


Vo


–





Io →





Io →





3Io →





3Io ↓





Lo





Lo





Lo





5.7 m





4.4 m





7.6 m





8.5 m





22.9 m at tower, and sags down 10 m at mid-span to 12.9 m.





7.6 m





7.8 m





Tower Base





345kV Double-Circuit Transmission Line


Scale:  1 cm = 2 m





Double conductor phase bundles, bundle radius = 22.9 cm, conductor radius = 1.41 cm, conductor resistance = 0.0728 Ω/km








Single-conductor ground wires, conductor radius = 0.56 cm, conductor resistance = 2.87 Ω/km








5 m





10 m





33 m





Tower Base





500kV Single-Circuit Transmission Line


Scale:  1 cm = 2 m





Triple conductor phase bundles, bundle radius = 20 cm, conductor radius = 1.5 cm, conductor resistance = 0.05 Ω/km








Single-conductor ground wires, conductor radius = 0.6 cm, conductor resistance = 3.0 Ω/km








10 m





5 m





39 m





Conductors sag down 10 m at mid-span





30 m





Earth resistivity ρ = 100 Ω-m








Page 1 of 8

_1160201394.unknown

_1160288174.unknown

_1359891574.unknown

_1423553646.unknown

_1423553657.unknown

_1359891611.unknown

_1359891976.unknown

_1359891586.unknown

_1359891503.unknown

_1359891525.unknown

_1329538563.unknown

_1329538876.unknown

_1160293218.unknown

_1160287281.unknown

_1160288126.unknown

_1160288155.unknown

_1160288156.unknown

_1160288139.unknown

_1160288004.unknown

_1160288096.unknown

_1160287303.unknown

_1160202255.unknown

_1160202315.unknown

_1160287218.unknown

_1160202272.unknown

_1160201677.unknown

_1156581388.unknown

_1156925423.unknown

_1160200364.unknown

_1160200714.unknown

_1160200418.unknown

_1156925432.unknown

_1156925398.unknown

_1156581352.unknown

_1156581374.unknown

_1156573988.unknown

_1156580608.unknown

_1156573474.unknown

