Solar_Power_Experiment_and_Equations_Mack_Grady_January_25_2013.doc

Report Details

Choose any of the solar stations, but take your measurements only when the short circuit current is at least 3.5A.  The weather forecast from www.weatherunderground.com can help you plan your schedule.
Your report should include graphs of I versus V, and P versus V.  Both actual data and Excel approximations should be plotted together.  When plotting with Excel, be sure to use the “scatter plot” option so that the non-uniform spacing between voltage points on the x-axis show correctly.  You should also work out numerical values for Equations (1) – (10) for the day and time of your measurements.
Overview

Incident sunlight can be converted into electricity by photovoltaic conversion using a solar panel.  A solar panel consists of individual cells that are large-area semiconductor diodes, constructed so that light can penetrate into the region of the p-n junction.  The junction formed between the n-type silicon wafer and the p-type surface layer governs the diode characteristics as well as the photovoltaic effect.  Light is absorbed in the silicon, generating both excess holes and electrons.  These excess charges can flow through an external circuit to produce power.

[image: image109.wmf])

1

(

-

BV

e

A


Figure 1.  Equivalent Circuit of a Solar Cell

Diode current 
[image: image1.wmf])

1

(

-

BV

e

A

 comes from the standard I-V equation for a diode, plotted above.  From Figure 1, it is clear that the current I that flows to the external circuit is 
[image: image2.wmf])

1

(

-

-

=

BV

sc

e

A

I

I

.  If the solar cell is open circuited, then all of the 
[image: image3.wmf]sc

I

 flows through the diode and produces an open circuit voltage of about 0.5-0.6V.  If the solar cell is short circuited, then no current flows through the diode, and all of the 
[image: image4.wmf]sc

I

 flows through the short circuit.
Since the Voc for one cell is approximately 0.5-0.6V, then individual cells are connected in series as a “solar panel” to produce more usable voltage and power output levels.  Most solar panels are made to charge 12V batteries and consist of 36 individual cells (or units) in series to yield panel Voc ≈ 18-20V.  The voltage for maximum panel power output is usually about 16-17V.  Each 0.5-0.6V series unit can contain a number of individual cells in parallel, thereby increasing the total panel surface area and power generating capability. 
[image: image110.wmf]0

5

0.0

0.6

Diode Volts

Diode Amps


Figure 2.  I-V Characteristics of Solar Panel
On a clear day, direct normal solar insolation (i.e., incident solar energy) is approximately 
[image: image5.wmf]2

/

1

m

kW

.  Since solar panel efficiencies are approximately 14%, a solar panel will produce about 140W per square meter of surface area when facing a bright sun.  High temperatures reduce panel efficiency.  For 24/7 power availability, solar power must be stored in deep-discharge batteries that contain enough energy to power the load through the nighttime and overcast days.  On good solar days in Austin, you can count on solar panels producing about 1kWH of energy per square meter.
An everyday use of solar power is often seen in school zone and other LED flashing signs, where TxDOT and municipal governments find them economical when conventional electric service is not readily available or when the monthly minimum electric fees are large compared to the monthly kWH used.  Look for solar panels on top of these signs, and also note their orientation.

The Solar Panels on ENS Rooftop
The ENS rooftop is equipped with six pairs of commercial “12V class” panels, plus one larger “24V class” commercial panel.  The panels are:

· three pair of British Petroleum BP585, (mono-crystalline silicon, laser grooved, each panel 85W, voltage at maximum power = 18.0V, current at maximum power = 4.7A, open circuit voltage = 22.3V, short circuit current = 5.0A).  These three pairs are connected to ENS212 stations 17, 18, and 19.

· two pair of Solarex SX85U (now BP Solar) (polycrystalline silicon, each panel 85W, voltage at maximum power = 17.1V, current at maximum power = 5.0A, open circuit voltage = 21.3V, short circuit current = 5.3A).  These two pairs are connected to ENS212 stations 15 and 16.
· one pair of Photowatt PW750-80 (multi-crystalline cells, each panel 80W, voltage at maximum power = 17.3V, current at maximum power = 4.6A, open circuit voltage = 21.9V, short circuit current = 5.0A).  This pair is connected to ENS212 station 21.
· one British Petroleum BP3150U, 150W panel (multicrystalline), open circuit voltage = 43.5V, short circuit current = 4.5A.  This is connected to ENS212 station 20.
Each of the seven stations is wired to ENS212 and has an open circuit voltage of approximately 40V and a short circuit current of approximately 5A.  The I-V and P-V characteristics for one of the panel pairs is shown in Figure 3.  The I-V curve fit equation for Figure 3 is


[image: image6.wmf](

)

1

00524

.

0

34

.

5

)

(

1777

.

0

-

-

=

V

e

V

I

.
[image: image111.wmf]m

m

I

V

P

=

max


Maximum Power

As seen in bottom figure of Figure 3, panels have a maximum power point.  Maximum power corresponds to Vm and Im in Figure 2.  Because solar power is relatively expensive (approx. $4-5 per watt for the panels, plus the same amount for batteries and electronics), it is important to operate panels at their maximum power conditions.  Unfortunately, Vm, Im, and the Thevenin equivalent resistance vary with light level.  DC-DC converters are often used to “match” the load resistance to the Thevenin equivalent resistance of the panel to maximize the power drawn from the panel.  These “smart” converters (often referred to as “tracking converters”) also charge the storage batteries in such a way as to maximize battery life.

Sun Position, Panel Orientation, and PV Harvest Prediction – The Big 10 Equations
Ideally, a solar panel should track the sun so that the incident solar rays are perpendicular to the panel surface, thus maximizing the capture of solar energy.  However, because of high wind loads, most panels are fixed in position.  Often, panel tilt (with respect to horizontal) is adjusted seasonally.  Orientation of fixed panels should be carefully chosen to capture the most energy for the year, or for a season.

The position of the sun in the sky varies dramatically with hour and season.  Sun zenith angle 
[image: image7.wmf]zenith

sun

q

 is expressed in degrees from vertical.  Sun azimuth 
[image: image8.wmf]azimuth

sun

f

 is expressed in degrees from true north.  Sun zenith and azimuth angles are illustrated in Figure 4.  

[image: image112.wmf])

1

(

-

-

=

BV

sc

e

A

I

I


Sun position angles are available in many references, and with different levels of complexity.  Some of the following equations were taken from the University of Oregon Solar Radiation Monitoring Laboratory (http://solardat.uoregon.edu/SolarRadiationBasics.html):

[image: image113.wmf]PV Station 13, Bright Sun, Dec. 6, 2002

0

1

2

3

4

5

6

0

5

10

15

20

25

30

35

40

45

V(panel) - volts

I - amps


Sun declination angle (in degrees) is


[image: image9.wmf]),

sin(

45

.

23

B

=

d

 where 


[image: image10.wmf])

81

(

365

360

-

=

n

B

 degrees , and


[image: image11.wmf]n

 = day of year (i.e., 1,2,3, … , 364,365).
(1)
Equation of time (in decimal minutes) is


[image: image12.wmf])

sin(

5

.

1

)

cos(

53

.

7

)

2

sin(

87

.

9

B

B

B

E

qt

-

-

=

.
(2)
Solar time (in decimal hours) is


[image: image13.wmf](

)

15

60

local

timezone

qt

local

solar

Longitude

Longitude

E

T

T

-

+

+

=

,
(3)
where

· 
[image: image14.wmf]local

T

 is local standard time in decimal hours,

· 
[image: image15.wmf]timezone

Longitude

 is the longitude at the eastern edge of the time zone (e.g., 
[image: image16.wmf]°

90

 for Central Standard Time). 

(Note – in the Solar_Data_Analyzer Excel spreadsheet program, 
[image: image17.wmf](

)

local

timezone

Longitude

Longitude

-

 is entered as “Longitude shift (deg).”  At Austin, with 
[image: image18.wmf]°

=

74

.

97

local

Longitude

, the longitude shift is 
[image: image19.wmf](

)

°

-

=

°

-

°

74

.

7

74

.

97

90

.  
Hour angle (in degrees) is


[image: image20.wmf](

)

solar

T

H

-

·

=

12

15

.
(4)
Cosine of the zenith angle is


[image: image21.wmf](

)

)

cos(

)

cos(

)

cos(

)

sin(

)

sin(

cos

H

L

L

zenith

sun

d

d

q

+

=

,
(5)
where 
[image: image22.wmf]L

 is the latitude of the location.

Solar azimuth comes from the following calculations.  Using the formulas for solar radiation on tilted surfaces, consider vertical surfaces directed east and south.  The fraction of direct component of solar radiation on an east-facing vertical surface is


[image: image23.wmf])

sin(

)

cos(

H

f

VE

d

=

.
(6)
The fraction of direct component of solar radiation on a south-facing vertical surface is


[image: image24.wmf])

cos(

)

sin(

)

cos(

)

cos(

)

sin(

H

L

L

f

VS

d

d

+

-

=

.
(7)
Equations (6) and (7) correspond to the projections, on the horizontal plane, of a vector pointing toward the sun.  By examining Figure 4, 
[image: image25.wmf]azimuth

sun

f

 can be found as follows:
If 
[image: image26.wmf]0

³

VE

f

, 
[image: image27.wmf]÷

÷

÷

ø

ö

ç

ç

ç

è

æ

+

-

=

-

2

2

1

cos

VS

VE

VS

azimuth

sun

f

f

f

f

 degrees,
If 
[image: image28.wmf]0

<

VE

f

, 
[image: image29.wmf]÷

÷

÷

ø

ö

ç

ç

ç

è

æ

+

+

=

-

2

2

1

cos

180

VS

VE

VS

azimuth

sun

f

f

f

f

 degrees.
(8)
As a check, all components of the sun radiation should account for the total, i.e.


[image: image30.wmf](

)

1

cos

2

2

2

=

+

+

zenith

sun

VS

VE

f

f

q

.

Illustrations of seasonal and daily sun positions for Austin are shown in Figures 5a and 5b.
An example of the step-by-step calculations for 3pm (i.e., 15.00 decimal hours) on October 25th in Austin follows.
[image: image114.wmf]PV Station 13, Bright Sun, Dec. 6, 2002

0.0

20.0

40.0

60.0

80.0

100.0

120.0

140.0

0

5

10

15

20

25

30

35

40

45

V(panel) - volts

P(panel) - watts


[image: image115.wmf]zenith

sun

q


Definitions from www.weatherground.com
	Twilight 
	This is the time before sunrise and after sunset where it is still light outside, but the sun is not in the sky. 

	Civil Twilight 
	This is defined to be the time period when the sun is no more than 6 degrees below the horizon at either sunrise or sunset. The horizon should be clearly defined and the brightest stars should be visible under good atmospheric conditions (i.e. no moonlight, or other lights). One still should be able to carry on ordinary outdoor activities. 

	Nautical Twilight 
	This is defined to be the time period when the sun is between 6 and 12 degrees below the horizon at either sunrise or sunset. The horizon is not defined and the outline of objects might be visible without artificial light. Ordinary outdoor activities are not possible at this time without extra illumination. 

	Astronomical Twilight 
	This is defined to be the time period when the sun is between 12 and 18 degrees below the horizon at either sunrise or sunset. The sun does not contribute to the illumination of the sky before this time in the morning, or after this time in the evening. In the beginning of morning astronomical twilight and at the end of astronomical twilight in the evening, sky illumination is very faint, and might be undetectable. 

	Length Of Day 
	This is defined to be the time of Actual Sunset minus the time of Actual Sunrise. The change in length of daylight between today and tomorrow is also listed when available. 

	Length Of Visible Light 
	This is defined to be the time of Civil Sunset minus the time of Civil Sunrise. 

	Altitude (or Elevation) 
	First, find your azimuth. Next, the Altitude (or elevation) is the angle between the Earth's surface (horizon) and the sun, or object in the sky. Altitudes range from -90° (straight down below the horizon, or the nadir) to +90° (straight up above the horizon or the Zenith) and 0° straight at the horizon. 

	Azimuth 
	The azimuth (az) angle is the compass bearing, relative to true (geographic) north, of a point on the horizon directly beneath the sun. The horizon is defined as an imaginary circle centered on the observer. This is the 2-D, or Earth's surface, part of calculating the sun's position. As seen from above the observer, these compass bearings are measured clockwise in degrees from north. Azimuth angles can range from 0 - 359°. 0° is due geographic north, 90° due east, 180° due south, and 360 due north again. 


	Hour Angle of the Sun 
	The Solar Hour Angle of the Sun for any local location on the Earth is zero° when the sun is straight overhead, at the zenith, and negative before local solar noon and positive after solar noon. In one 24-hour period, the Solar Hour Angle changes by 360 degrees (i.e. one revolution). 

	Mean Anomaly of the Sun 
	The movement of the Earth around the Sun is an ellipse. However, if the movement of the Earth around the Sun were a circle, it would be easy to calculate its position. Since, the Earth moves around the sun about one degree per day, (in fact, it's 1/365.25 of the circle), we say the Mean Anomaly of the Sun is the position of the Earth along this circular path. The True Anomaly of the Sun is the position along its real elliptical path. 

	Obliquity 
	Obliquity is the angle between a planet's equatorial plane and its orbital plane. 

	Right Ascension of the Sun 
	The Celestial Sphere is a sphere where we project objects in the sky. We project stars, the moon, and sun, on to this imaginary sphere. The Right Ascension of the Sun is the position of the sun on our Celestial Sphere 

	Solar Noon (and Solar Time) 
	Solar Time is based on the motion of the sun around the Earth. The apparent sun's motion, and position in the sky, can vary due to a few things such as: the elliptical orbits of the Earth and Sun, the inclination of the axis of the Earth's rotation, the perturbations of the moon and other planets, and of course, your latitude and longitude of observation. Solar Noon is when the sun is at the highest in the sky, and is defined when the Hour Angle is 0°. Solar Noon is also the midpoint between Sunrise and Sunset. 

	Sun Declination 
	The Declination of the sun is how many degrees North (positive) or South (negative) of the equator that the sun is when viewed from the center of the earth. The range of the declination of the sun ranges from approximately +23.5° (North) in June to -23.5° (South) in December. 


Panel Orientation and Solar Incident Angle
[image: image116.wmf]azimuth

sun

f

Unless there are obstructions, panels should face due south (i.e., have an azimuth angle of 180º).  Recommended panel tilt angles (above horizontal) are latitude + 15º in winter, and latitude – 15º in summer.  In Austin, with latitude = 30º, these recommendations correspond to 45º in winter, and 15º in summer.  If no seasonal adjustments are made, then the best fixed panel tilt angle is latitude (i.e., 30º in Austin).  The tilt angles of our panels are adjusted twice each year, at the spring and fall equinoxes.  Our tilt angles are 20o in summer, and 45o in winter.
[image: image117.wmf]11

.

13

-

=

d


[image: image118.wmf]21

.

16

=

qt

E


The angle between the rays of the sun and a vector perpendicular to the panel surface is known as the angle of incidence (
[image: image31.wmf]incident

b

).  The cosine of 
[image: image32.wmf]incident

b

 is found by first expressing a unit vector pointed toward the sun, and a unit vector perpendicular to the panel surface, and then taking the dot product of the two unit vectors.  When 
[image: image33.wmf]1

)

cos(

=

incident

b

, then the sun’s rays are perpendicular to the panel surface, so that maximum incident solar energy is captured.  The expressions follow.
Considering Figure 4, the unit vector pointed toward the sun is


[image: image34.wmf][

]

[

]

[

]

z

y

x

sun

a

a

a

a

ˆ

cos

ˆ

sin

sin

ˆ

cos

sin

ˆ

zenith

sun

azimuth

sun

zenith

sun

azimuth

sun

zenith

sun

q

f

q

f

q

-

+

=

.

Considering Figure 6, the unit vector perpendicular to the panel surface is


[image: image35.wmf][

]

[

]

[

]

z

y

x

panel

a

a

a

a

ˆ

cos

ˆ

sin

sin

ˆ

cos

sin

ˆ

tilt

panel

azimuth

panel

tilt

panel

azimuth

panel

tilt

panel

q

f

q

f

q

-

+

=


The dot product of the two unit vectors is then


[image: image36.wmf][

]

azimuth

panel

tilt

panel

azimuth

sun

zenith

sun

incident

f

q

f

q

b

cos

sin

cos

sin

ˆ

ˆ

cos

=

·

=

panel

sun

a

a



[image: image37.wmf][

]

azimuth

panel

tilt

panel

azimuth

sun

zenith

sun

f

q

f

q

sin

sin

sin

sin

+



 EMBED Equation.3  [image: image38.wmf][

]

tilt

panel

zenith

sun

q

q

cos

cos

+

.
Combining terms yields


[image: image39.wmf][

]

azimuth

panel

azimuth

sun

azimuth

panel

azimuth

sun

tilt

panel

zenith

sun

incident

f

f

f

f

q

q

b

sin

sin

cos

cos

sin

sin

cos

+

=



[image: image40.wmf]tilt

panel

zenith

sun

q

q

cos

cos

+

.

Simplifying the above equation yields the general case,

[image: image41.wmf](

)

tilt

panel

zenith

sun

azimuth

panel

azimuth

sun

tilt

panel

zenith

sun

incident

q

q

f

f

q

q

b

cos

cos

cos

sin

sin

cos

+

-

=

.
(9)
Some special cases are
1.  Flat panel (i.e., 
[image: image42.wmf]0

=

tilt

panel

q

).  Then, 


[image: image43.wmf]zenith

sun

incident

q

b

cos

cos

=

.

2.  Sun directly overhead (i.e., 
[image: image44.wmf]0

=

sun

zenith

q

).  Then, 


[image: image45.wmf]tilt

panel

incident

q

b

cos

cos

=

.

3.  Equal azimuth angles (i.e., azimuth tracking, 
[image: image46.wmf]azimuth

panel

azimuth

sun

f

f

=

).  Then, 

[image: image47.wmf](

)

tilt

panel

zenith

sun

tilt

panel

zenith

sun

tilt

panel

zenith

sun

incident

q

q

q

q

q

q

b

-

=

+

=

cos

cos

cos

sin

sin

cos

.

4.  Sun zenith angle equals panel tilt angle (i.e., zenith tracking, 
[image: image48.wmf]tilt

panel

zenith

sun

q

q

=

).  Then, 


[image: image49.wmf](

)

zenith

sun

azimuth

panel

azimuth

sun

zenith

sun

incident

q

f

f

q

b

2

2

cos

cos

sin

cos

+

-

=

.

To illustrate the general case, consider the following example:  3pm (standard time) in Austin on October 25.  The sun position is

[image: image50.wmf]azimuth

sun

f

 = 228.7º, 
[image: image51.wmf]zenith

sun

q

 = 58.8º, so that 
[image: image52.wmf]z

y

x

sun

a

a

a

a

ˆ

517

.

0

ˆ

643

.

0

ˆ

565

.

0

ˆ

-

-

-

=

,
and the panel angles are

[image: image53.wmf]azimuth

panel

f

 = 190º, 
[image: image54.wmf]tilt

panel

q

= 45º, so that 
[image: image55.wmf]z

y

x

panel

a

a

a

a

ˆ

707

.

0

ˆ

1228

.

0

ˆ

696

.

0

ˆ

-

-

-

=

.
Evaluating the dot product yields 
[image: image56.wmf]incident

b

cos

 = 0.838, so 
[image: image57.wmf]incident

b

 = 33.1º.
Solar Radiation Measurements

The three most important solar radiation measurements for studying solar panel performance are global horizontal (GH), diffuse horizontal (DH), and direct normal (DN).  GH is “entire sky,” including the sun disk, looking straight up.  DH is “entire sky,” excluding the sun disk, looking straight up.  DN is facing directly toward the sun.  The units for GH, DH, and DN are W/m2.

The direct measurement of DN requires a sun tracking device.  The Sci Tek 2AP tracker takes DN, GH, and DH readings every five minutes using three separate thermocouple sensors.  The DN sensor tracks and sees only the disk of the sun.  The GH sensor points straight up and sees the entire sky with sun disk.  The DH sensor points straight up, but a shadow ball blocks the disk of the sun, so that it sees entire sky minus sun disk.
Rotating shadowband pyranometers use one PV sensor, pointed straight up, to measure GH and DH every minute, and then save average values every 5 minutes.  Once per minute, the shadow band swings over, and when the shadow falls on the sensor, the DH reading is taken.  Using GH and DH, the rotating shadow-band pyranometer estimates DN.  
[image: image119.wmf]74

.

7

-


[image: image120.wmf]00

.

15

=

local

T


Rotating shadow band pyranometers are simple in that they do not track the sun.  Instead, they merely rotate a shadow band every minute across the PV sensor.  When there is no shadow on the sensor, the sensor reads GH.  When the shadow falls on the sensor, the sensor reads DH.
Computing Incident Solar Power on a Panel Surface

To compute the incident solar power on a panel surface, we assume that the panel captures all of the diffuse horizontal (DH) power, plus the fraction of (GH – DH) that is perpendicular to the panel surface.  

[image: image58.wmf])

cos(

)

cos(

)

(

incident

zenith

sun

incident

DH

GH

DH

P

b

q

·

-

+

=

 W/m2.
(10)
The above value, in W/m2, is then multiplied by the panel surface area to yield total incident solar power 
[image: image59.wmf]incident

P

.  Multiplying by panel efficiency yields maximum expected electrical power output.
Because panels are rated at 1kW/m2, (10) is also the estimated panel W output per kW rated.  Integrate over all hours of the day and divide by 1000, and you get estimated kWH output per kW rated (i.e., the PV daily harvest).
To avoid serious overcorrection when the sun is near the horizon, ignore the 
[image: image60.wmf])

cos(

zenith

sun

q

 term when 
[image: image61.wmf]zenith

sun

q

 > 85º.  For the 3pm, October 25th example, the readings are 
[image: image62.wmf]2

/

535

m

W

GH

=

, and 
[image: image63.wmf]2

/

38

m

W

DH

=

,


[image: image64.wmf]panel

incident

A

P

·

ú

û

ù

ê

ë

é

°

·

°

-

+

=

)

1

.

33

cos(

)

9

.

58

cos(

)

38

535

(

38

 = 
[image: image65.wmf]2

/

  

844

m

W

A

panel

·

,
which means that a PV panel or array would produce 844 W per kW rated power.

[image: image121.wmf]75

.

14

=

solar

T


Computing Sunrise and Sunset Times
To reduce the volume of data stored and processed, it is best to start and stop solar data loggers just before sunrise and just after sunset.  I developed the following empirical formulas for sunrise and sunset, which are applicable to north latitudes 25° through 45°.  The worst-case error is 6 minutes.  To take into account the error and the fact that the formulas apply to the situation where one-half of the sun is above the horizon, start/stop 15 minutes before/after the computed values.


[image: image66.wmf]÷

ø

ö

ç

è

æ

·

+

·

·

+

÷

ø

ö

ç

è

æ

·

+

·

·

+

=

180

365

4

sin

180

365

2

sin

 

p

p

p

p

E

DOY

D

C

DOY

B

A

Sunrise

rise

rise

,
where 
[image: image67.wmf]Sunrise

 is the decimal minute of the day at the eastern edge of the time zone, and

[image: image68.wmf]DOY

 is day of the year (1 through 365, ignore leap year), 


[image: image69.wmf]360

=

rise

A

, 
[image: image70.wmf]94

=

rise

C

, 
[image: image71.wmf]0

.

9

=

D

, 
[image: image72.wmf]1

.

20

=

E

,


[image: image73.wmf]2

2

1

0

L

B

L

B

B

B

·

+

·

+

=

, where 
[image: image74.wmf]L

 is latitude north,

[image: image75.wmf]3

.

21

0

=

B

, 
[image: image76.wmf]07

.

0

1

=

B

, 
[image: image77.wmf]0371

.

0

2

=

B

.
Sunset follows the same formula, but replace 
[image: image78.wmf]rise

A

 with 
[image: image79.wmf]set

A

, and 
[image: image80.wmf]rise

C

 with 
[image: image81.wmf]set

C

, where


[image: image82.wmf]720

+

=

rise

set

A

A

,
[image: image83.wmf]168

-

=

rise

set

C

C

.
To correct for locations west of the eastern edge, recall that the sun moves 15 degrees of longitude in one hour, which corresponds to 4 minutes delay per degree of longitude. 
[image: image84.jpg]



Rotating Shadow Band Monitor at Toyah, TX

Master’s Clear Sky Equations
The Master’s textbook, G. M. Masters, Renewable and Efficient Electric Power Systems, John Wiley & Sons, 2004, gives a set of equations knows as “clear sky” equations.  These equations predict solar intensity for cloudless, very clear days that are common in West Texas, especially in winter.  They have proven very useful for checking the reasonableness of measured data on very clear days, and for giving “best case” daily harvest predictions.  The twelve steps for predicting the incident solar energy on a solar panel for a given day and time is given here.  And, given a year of actual data, it is possible to adjust the variables of these equations to account for the local atmosphere.
1.  Extraterrestrial Solar Insolation I0 (just outside Earth’s atmosphere)
[image: image122.wmf]25

.

41

-

=

H

[Master’s 7.20, Solar_Data_Analyzer Col. N]


[image: image85.wmf]ú

û

ù

ê

ë

é

+

·

=

)

365

360

cos(

034

.

0

1

0

N

SC

I

 W/m2 , where

SC (solar constant) = 1.377 kW/ m2.

N = Day of Year,

Note from the table:  
[image: image86.wmf]0

I

 is max in winter, min in summer, nominal at equinoxes, and has 6.8% peak-to-peak variation.

The above equation is not actually used in the following Clear Sky predictions.
2.  Air Mass Ratio m (relative atmosphere travel distance to reach Earth’s surface)
[Master’s 7.4, Solar_Data_Analyzer Col. O]

[image: image87.wmf])

cos(

1

sun

zenith

m

q

=


3.  Apparent Extraterrestrial Flux A
[image: image123.wmf]81

.

58

=

zenith

sun

q

[Master’s 7.22, Solar_Data_Analyzer Col. P]

[image: image88.wmf]ú

û

ù

ê

ë

é

-

·

+

=

)

275

(

365

360

sin

75

1160

N

A

 W/m2 , 

or in general form,


[image: image89.wmf]ú

û

ù

ê

ë

é

-

·

+

=

)

(

365

360

sin

2

1

A

N

N

A

A

A

 W/m2 , 

where

Note from the table:  A is max in winter, min in summer, nominal at equinoxes, and has 12.9% peak-to-peak variation
4.  Optical Depth k

[Master’s 7.23, Solar_Data_Analyzer Col. Q]

[image: image90.wmf]ú

û

ù

ê

ë

é

-

·

+

=

)

100

(

365

360

sin

035

.

0

174

.

0

n

k

, 

or in general form 


[image: image91.wmf]ú

û

ù

ê

ë

é

-

·

+

=

)

(

365

360

sin

2

1

K

N

N

K

K

k


5.  Beam Reaching Earth IB
[Master’s 7.21, Solar_Data_Analyzer Col. R]

[image: image92.wmf]km

B

Ae

I

-

=

 W/m2 

6.  Sky Diffuse Factor C

[Master’s 7.28, Solar_Data_Analyzer Col. S]

[image: image93.wmf]ú

û

ù

ê

ë

é

-

·

+

=

)

100

(

365

360

sin

04

.

0

095

.

0

n

C

,

or in general form,


[image: image94.wmf]ú

û

ù

ê

ë

é

-

·

+

=

)

(

365

360

sin

2

1

C

N

N

C

C

C


7.  Diffuse Radiation on Horizontal Surface IDH
[Master’s 7.27, Solar_Data_Analyzer Col. T]

[image: image95.wmf]B

DH

I

C

I

·

=

 W/m2
8.  Beam Normal to a Panel IBC
[Master’s 7.24, Solar_Data_Analyzer Col. U]

[image: image96.wmf])

cos(

incident

B

BC

I

I

b

·

=

 W/m2
9.  Beam on Horizontal Surface IBH
[Master’s 7.25, Solar_Data_Analyzer Col. V]

[image: image97.wmf])

cos(

sun

zenith

B

BH

I

I

q

·

=

 W/m2
10.  Diffuse Radiation on Panel IDC 

[Master’s 7.29, Solar_Data_Analyzer Col. W]

[image: image98.wmf]÷

÷

÷

ø

ö

ç

ç

ç

è

æ

+

=

2

cos

1

panel

tilt

DH

DC

I

I

q

 W/m2
11.  Reflected on Panel IRC (from the ground and surrounding objects)

[Master’s 7.30, Solar_Data_Analyzer Col. X]

[image: image99.wmf](

)

÷

÷

÷

ø

ö

ç

ç

ç

è

æ

-

·

+

·

=

2

cos

1

panel

tilt

DH

BH

RC

I

I

I

q

r

 W/m2 ,
where ground reflectance 
[image: image100.wmf]r

 is typically 0.2, but can be as large as 0.8 for fresh snow.
12.  Total Clear Sky Insolation on Panel IC 

[Master’s 7.32, Solar_Data_Analyzer Col. Y]


[image: image101.wmf]RC

DC

BC

C

I

I

I

I

+

+

=

 W/m2 
The Experiment

Your assignment is to measure the I-V and P-V characteristics of a solar panel pair, plot the points, determine maximum power, estimate panel efficiency, and use the Excel Solver to approximate the I-V and P-V curves using


[image: image102.wmf])

1

(

-

-

=

BV

sc

e

A

I

I

, 
[image: image103.wmf][

]

)

1

(

-

-

·

=

=

BV

sc

e

A

I

V

VI

P

,

where the Solver estimates coefficients Isc, A, and B from your measured I-V data set.  See the Appendix for a description of the Excel Solver.

Experimental Procedure

You will need about 30 minutes to take the experimental data.  Go to an available panel station, and check the short circuit current.  Take your measurements when the short circuit current is at least 3.5A (try for a sunny day, between 11:30am and 1:30pm. CDT (corresponding to solar noon, plus or minus 1 hour).  (Note - weather site www.weatherunderground.com can help you make your plans for upcoming days.)  Then, using the voltage at the panel (i.e., the left-most meter in the yellow solar panel interface box), and the panel ammeter (the right-most meter), perform the following steps given below, recording and plotting your data on the experimental form and on the graph as you go:
[image: image124.wmf]6421

.

0

-

=

VE

f


Form and Graph for Recording and Plotting Your Readings as You Take Them

[image: image125.wmf]5651

.

0

=

VS

f

(have this page signed by Dr. Grady before beginning your report)

Panel Station = ____ Date and Time of Measurements= ___________, Sky Conditions = _____

	Vpanel*
	Ipanel*
	P (i.e., Vpanel ● Ipanel )
	Notes

	Voc =
	
	
	Open circuit condition

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	Isc =
	
	Short Circuit Condition


* Vpanel (i.e., at the panel) is the left-most meter in the yellow interface box, and Ipanel is the right-most meter.

Steps

1. Measure the panel pair’s open circuit voltage, and record in the table and on the graph.  The current is zero for this case.
2. Short the output terminals with one of the red shorting bar or with a wire.  Measure the short circuit current and panel pair voltage.  Record both and add the point to your graph.  The panel voltage will be small for this condition.

3. Connect one of the “solar testers” (i.e., the heavy-duty variable resistor boxes with the large knobs) to the panel pair output terminals.  You will use the variable rheostat and switch to sweep the entire I-V curve.
[image: image126.wmf]7

.

228

=

azimuth

sun

f


4. Beginning with the near open circuit condition, (i.e., maximum resistance), lower the solar tester resistance so that the panel pair voltage decreases from open circuit toward zero in steps of approximately 2V between 25-40V, and in 5V steps below 25V.  Record panel pair voltage and current at each step, and hand plot I versus V results as you go.  If your points do not form a smooth curve, you may want to retake the outliers.  Cloud movement can cause these variations.
The laboratory measurement portion of the experiment is now completed.  Your graph should be fairly smooth and free of outlying points.  You can now leave the lab bench.  

Next, you will
5. Download Excel file PV_Plots_Solver.xls from the course web page, and then enter your V and I values in Excel.  Modify the plot command so that all the data for your experiment will be plotted.  Plot I versus V points, and P = V • I versus V points using the “scatter plot” option.

6. Visually estimate Vm, Im, and Pmax (i.e., peak power conditions) from your plots.
7. Use the Excel Solver to compute coefficients Isc, A, and B from your I-V data.  Modify the Solver command so that all your data will be included in the calculations.  Superimpose the Solver equations on the I-V and P-V graphs of Step 5.  See the Appendix for Solver instructions.  Use your Solver graph to estimate Pmax.

Now, use the following steps to estimate panel pair efficiency:

8. Go to the class web page and download the Excel spreadsheet and solar data files
Solar_Data_Analyzer.xls, and

SOLAR_DATA_through_XXX.zip, (XXX is the last data day in the zip)
Note – the 1-minute data averages are recorded by a shadow band tracker atop ETC and are updated daily on the web page while EE462L is being taught.

9. Display the data for your day (note – these data are given in Central Standard Time).  
10. For the minute that best represents your time of measurements, work through the Big 10 equations.

11. Compare your Big 10 equations to the Solar_Data_Analyzer spreadsheet values for your day/minute (see Appendix B).
12. For your day, use the Solar_Data_Analyzer spreadsheet as demonstrated in class to predict Method 1 daily kWh per installed kW for 

· for fixed panel azimuth = 180, and panel tilts 20, 30, and 40 degrees, 

· for single axis tracking, azimuth = 180, tilt = 20 and 30,

· for two-axis tracking.

Interpret and comment on the results. 

Appendix A:  Using the Excel Solver to Curve-Fit Measured Data
The Excel Solver is not part of the “Typical User” installation.  Check to see if the Solver is activated in your Excel installation by selecting “Tools,” and then “Add-Ins.”  If Solver is checked, it is ready for use.  Otherwise, check “Solver Add-In,” and Excel will guide you through the steps.  It will probably be necessary to insert your Excel installation CD rom.

[image: image104.png]Add-Ins available:
ey TooPak-VEA I x

I utosave Addin
[T ConditonalSum wizard =
I Euro Currency Tools
I ermet Assistant Ve arowse
I Lookup wierd 2
I 15 Query Adden
I oveC Addin
I Report Manager
v B

ohver Addin

Tool For aptinizaton and equation ching





To use Solver, refer to the following page.  Enter your V and I data, and establish cells for I equation coefficients Isc, A, and B.  Then, key-in the I equation shown previously to form a column of predicted currents, linking each cell to the Isc, A, and B cells.  Next, establish a column of squared errors for current, and then one cell with sum of squared errors.

[image: image127.wmf]Solar Zenith versus Azimuth at Austin

22nd Day of Dec, Jan, Feb, Mar, Apr, May, Jun

(Sun hrs/day.  

Dec=10.0,Jan=10.3,Feb=11.0,Mar=12.0,Apr=12.8,May=13.6,Jun=13.9)

0

10

20

30

40

50

60

70

80

90

0

30

60

90

120

150

180

210

240

270

300

330

360

Azimuth (South = 180)

Zenith (Degrees from Vertical)


Now, under “Tools,” select “Solver.”  The following window will appear.  Enter your “Target Cell” (the sum of squared errors cell), plus the “Changing Cells” that correspond to Isc, A, and B.  It is for your starting values for Isc, A, and B are reasonable.  You should probably use the A and B values shown above as your starting point.  Use your own measured short circuit current for Isc.
[image: image105.png]Parameters [z]x]

Set Torget Cal S = Sohve
EpalToi  Cs Gmg Cydwesh [0 Close
By Changing Cels: —=
o575 Guess
Subject o the Constraits: Qptons
|
Reset Al
peete || ————
= e





Be sure to request “Min” to minimize the error, and then click “Solve.”

[image: image106.png]Salver found a soution. Al constraints and aptimalty
conitions are satisfed. Reparts

 egp Solver Salicr

€ Restore Original Values

== Tosmn

Help

21|





If successful, click “OK” and then plot your measured I, and your estimated I, versus V to make a visual comparison between the measured and estimated currents.  Use the scatter plot option to maintain proper spacing between voltage points on the x-axis.

If unsuccessful when curve fitting, try changing Isc, A, or B, and re-try.

Appendix B:  Daily Analysis of Solar Radiation Data Taken by Rotating Shadow Band Radiometers, Using Solar_Data_Analyzer.xlsm Spreadsheet


Put the daily data files (unzipped) and spreadsheet in a directory named C:\SOLAR_DATA, and then 

· Double-click on Solar_Data_Analyzer_130123.xlsm.  Enable macros (you can trust me!) 

· In order to speed up execution, pull up the bottom of the spreadsheet screen so that the graphs are hidden.  If the graphs are displayed during execution, they will be continually updated as solar data files are read, which slows down execution.

[image: image128.wmf]Solar Zenith versus Azimuth at Austin

22nd Day of Jun, Jly, Aug, Sep, Oct, Nov, Dec

(Sun hrs/day.  Jun=13.9,Jly=13.6,Aug=12.8,Sep=12.0,Oct=11.0,Nov=10.3,Dec=10.0)

0

10

20

30

40

50

60

70

80

90

0

30

60

90

120

150

180

210

240

270

300

330

360

Azimuth (South = 180)

Zenith (Degrees from Vertical)


· Press “Execute” in the top left corner, and the program interface will appear

[image: image129.wmf]tilt

panel

q


· Select the station (e.g., BAYLOR_SOLAR) 

· Insert the year, and then day of year (three digits) in the day box

· Click "READ". 

The spreadsheet is slow to read the day, perhaps 2-minues, because it is building graphs that describe the day and predict solar panel performance with fixed, single-axis, and double-axis tracking.  When the spreadsheet is actually reading the data file, you will see minute-by-minute updates in the green boxes near the top of Column J. 

· Once the program has finished reading the day, you will see the green “OK” light and the fields in the “Single Day Analysis” box will be populated.

[image: image107.png] Read Solar Radiation Data

Single Day Analysis
patn | Proceed Without Logger Data ClocksurvseClock Sunset
C:\SOLAR_DATA 0732 1746
[~ File Names (1 minute data spacing only) Decmal Sunrise  Decimal Sunset.
& BAYLOR_SOLAR dat 7.5 777
Cromamar fria
n—ﬂa;ﬂnﬂyﬂmhm 1 Ceerser L=
273 for Set. 0, etc) vetedt [ 453
i verPA [ o0
| | Fie Name (refore sbove yearfday s nserted)

Notes -The program passes information
o the spreadsheet, uhich performs the
caladations, When firished, use the.
STOP PROGRAM button 5o that the fles
are properly dosed.

Expected kith per installed KW of solar
panels i the same as the kWh/m2 values.
shown here.

Loop
StartDay  StopDay.
o1 15
™ nLoop

o
ol

- TitStepsize -Deg ——|
s Cn O
- Azimuth Stepsize -Deg —|
Cs 6w O

139,4,2013,19,702,.057,-.328,.325,.001,-.326,-.328,~.325,0,0,0,0,0,0,54.75,1, 1, 1,1

139,4,2013,19,703,.072,-.328,.325, 002,325, 328,-635,0,0,0,0,0,0,54.75,2, ,70,1

Last Two Lines Read from Solar Radiation Data Fle:

139,4,2013,19, 1814,.159,-.325,.328, 710,327,327, 327,0,0,0,0,0,0,54.75,4,1,15,1

139,4,2013,19, 1815, 031,325,328, 3710, 327,-.327,-.327,0,0,0,0,0,0,54.75,8,24,1,1

Messages and Errors

‘Opening Fie C-\SOLAR_DATAIBAYLOR_SOLAR_2013_015_JAN_19.dat
ok





· You can click "STOP" to reset, and then start over with a new day. 

· Print the spreadsheet, black-and-white is OK, which will produce one page that summarizes the day and also points out any measurement problems

[image: image130.wmf]tilt

panel

q


The example shown above (Baylor, Jan. 19, 2013) is a day with some sun, interrupted by cloud shadows.  Sunny periods are when the measured GH has peaks (purple curve in left graph, black curve in right graph).  Indication of proper shadow band movement is shown where the green curve (DH) in the right graph is below or borders the black curve (GH).  If DH consistently rises to GH, there is either no measurable sun beam, or the shadow band is stuck.

Keep the prints in a three-ring binder.  Also, keep a spreadsheet table that shows for each day the values of

· Station Name, Year, Day of Year, Month (name), Day of Month, Meas. GH, Clear Sky GH, Measured PA, Clear Sky PA, PA Calc. Method 1, and 

· and a column for observations such as odd events, and any indications of suspect data such as stuck shadow band or missing values.

More example days follow:

[image: image131.jpg]



Baylor, Jan. 20, 2013

Clear sky conditions.  Shadow band stops operating just before 15:00.  While not obvious to the user, the GH, DH readings are about 20% high because calibration had not yet been performed.

[image: image132.jpg]



Toyah, Jan. 22, 2013

Clear sky conditions.  In addition to GH, DH, Toyah has a PA sensor and a backup GH sensor

[image: image133.jpg]



Toyah, Jan. 01, 2013

Clear air with moving shadows from white cumulus clouds until 14:30, then becoming mostly cloudy.  Note the high peaks in GH due to an intense sun surrounded by bright white clouds.  The peaks are higher than clear sky conditions on the previous figure.

Appendix C:  National and State Solar Insolation Data

Direct Solar Insolation Levels

(courtesy of Texas State Energy Conservation Office, www.infinitepower.org)

[image: image134.png]Licor GH
(inexpensive
backup)





Appendix D:  Magnetic Declination
[image: image108.jpg]Magnetic Declination Map of North America for the year 2010

130w 120w nww 100W

The term magnetic declination (also known as magnetic variation) refers to the angle between the magnetic north (MN - compass north ) and true north

(TN - true north) at any given latitude /longitude. The black contour line shows the imaginary line along which the declination is zero (MN and TN converges).
‘The magnetic declination increases as one moves east or west from this line. The red line shows the negative (west) declination contours and the blue line
shows the positive (east) declination contours. The degrees of declination required in order to orient the compass with the map is added east of this line and
subtracted west of this line. (e.g.. 10 degrees east would indicate that MN lies 10 degrees clockwise from the TN). Magnetic declination gradually changes

with time and location. The dotted grey lines show the expected annual change in the magnetic declination in arc minutes. The above map is produced from
the World Magnetic Model (WMM 2010) for the year 2010





n-type








p-type





–


V


+





I





Photons





Junction








External circuit


(e.g., battery, lights)





Isc





–


V


+





I





� EMBED Equation.3  ���








External circuit


(e.g., battery, lights)





�





V





I





Isc





Voc





Im





Vm





, where A, B, and especially Isc vary with solar insolation





0





0





Increasing


solar insolation





� EMBED Equation.3  ���





Maximum power point





� EMBED Equation.3  ���





�





PV Station, Bright Sun





�





PV Station, Bright Sun





Figure 3.  I-V and P-V Characteristics for One of the Panel Pairs


(data points taken by loading the panel pair with a variable load resistor)








Figure 4.  Sun Zenith and Azimuth Angles





West





North


(x axis)





Line perpendicular to horizontal plane





East


(y axis)





Horizontal plane





Up (−z axis)





� EMBED Equation.3  ���





� EMBED Equation.3  ���





Note – because of magnetic declination, a compass in Austin points approximately 7º east of north.





First Day of�
n�
First Day of�
n�
�
January�
1�
July�
182+�
�
February�
32�
August�
213+�
�
March�
60+�
September�
244+�
�
April�
91+�
October�
274+�
�
May�
121+�
November�
305+�
�
June�
152+�
December�
335+�
�
+ add 1 for leap years





Input�
n = 298th day�
�
Compute�
B = 214.0º�
�
Compute�
� EMBED Equation.3  ���º�
�
Compute�
� EMBED Equation.3  ��� decimal minutes�
�
Input�
Longitude = 97.74º�
�
Input�
Longitude shift = � EMBED Equation.3  ���º�
�
Input�
� EMBED Equation.3  ��� decimal hours�
�
Compute�
� EMBED Equation.3  ��� decimal hours�
�
Compute�
� EMBED Equation.3  ���º�
�
Input�
Latitude (L) = 30.29º�
�
Compute�
� EMBED Equation.3  ���º�
�
Compute�
� EMBED Equation.3  ����
�
Compute�
� EMBED Equation.3  ����
�
Compute�
� EMBED Equation.3  ���º�
�






output





output





Figure 5a.  Sun Position for Winter and Spring Seasons in Austin


(note – solar noon in Austin occurs at approximately 12:30pm CST)





Figure 5b.  Sun Position for Summer and Fall Seasons in Austin


(note – solar noon in Austin occurs at approximately 12:30pm CST)





�





�





� EMBED Equation.3  ���





 Line perpendicular to horizontal plane





� EMBED Equation.3  ���





Horizontal plane





Figure 6.  Panel Tilt Angle





 Line perpendicular to panel surface





 Edge of panel





All panels atop ENS have azimuth angle = 190o





View Facing Front of ENS Panels (i.e., looking toward north)


(Note – areas shown are for individual panels, so for a pair, double the values shown)








Station 18


BP








Station 19


BP





Station 18


BP








Station 17


BP





Station 16


Solarex








Station 16


Solarex





Station 19


BP





Station 17


BP





Station 15


Solarex








Station 15


Solarex








Station 21


Photowatt








Station 21


Photowatt





Area of each panel is 0.54m2





Area of each panel is 0.52m2





Area of each panel is 0.60m2





Station 20


BP








Area of this panel is 1.04m2





�





Panels atop ENS





�





�





Rotating Shadowband Pyranometers





�





NREL Sci Tec Two-Axis Tracker





�





N�
Approx. Value of Bracketed Term�
�
1�
1 + 0.034�
�
90�
1�
�
180�
1 – 0.034�
�
270�
1�
�
365�
1 + 0.034�
�






N�
Approx. Value of Second term�
�
1�
74�
�
90�
3�
�
180�
-75�
�
270�
6�
�
365�
75�
�






�





Voltage at solar panel





Voltage at lab bench


(don’t record)





Current





0V	10V	20V	30V	40V	50V





6A








5A








4A








3A








2A








1A








0A





≈2V spacing for V > 25V





≈5V spacing for V ≤ 25V





Staple this sheet to the back of your report





�





PV Station 13








Isc=


5.340E+00














A=


5.232E-03














B=


1.778E-01





Vpanel


I


I equation


(I error)^2


Ppanel = VI





39


0


-1.837E-02


0.000337


0.0





35


2.65


2.711E+00�
0.003701


92.8





30


4.3


4.262E+00


0.001448


129.0





25


4.95


4.900E+00


0.002531


123.8





20


5.15


5.162E+00


0.000142


103.0





4


5.3


5.334E+00


0.001179


21.2














0.009338








�
�
�
�
�
�
�
�
�
�
�
�
�
�
�
�
�
�
�
�
�
�
�
�
�
�
�
�
�






Coefficients of I Equation





Currents Predicted by I Equation





Sum of Squared Errors





Individual Squared Errors





Add rows so you can enter all your data points





�





�





AVERAGE DIRECT NORMAL INSOLATION MAP LEGEND�
�
COLOR�KEY�
per day�(kWh/m2-day) �
per YEAR�
�
�
�
(MJ/m2)�
(quads/100 mi2)�
�
� INCLUDEPICTURE "http://www.infinitepower.org/images/color2.gif" \* MERGEFORMATINET ����
<3.0�
<3,940�
<1.0�
�
� INCLUDEPICTURE "http://www.infinitepower.org/images/color4.gif" \* MERGEFORMATINET ����
3.0 - 3.5�
3,940 - 4,600�
1.0 - 1.1�
�
� INCLUDEPICTURE "http://www.infinitepower.org/images/color6.gif" \* MERGEFORMATINET ����
3.5 - 4.0�
4,600 - 5,260�
1.1 - 1.3�
�
� INCLUDEPICTURE "http://www.infinitepower.org/images/color7.gif" \* MERGEFORMATINET ����
4.0 - 4.5�
5,260 - 5,910�
1.3 - 1.5�
�
� INCLUDEPICTURE "http://www.infinitepower.org/images/color9.gif" \* MERGEFORMATINET ����
4.5 - 5.0�
5,910 - 6,570�
1.5 - 1.6�
�
� INCLUDEPICTURE "http://www.infinitepower.org/images/color10.gif" \* MERGEFORMATINET ����
5.0 - 5.5�
6,570 - 7,230�
1.6 - 1.8�
�
� INCLUDEPICTURE "http://www.infinitepower.org/images/color11.gif" \* MERGEFORMATINET ����
5.5 - 6.0�
7,230 - 7,880�
1.8 - 1.9�
�
� INCLUDEPICTURE "http://www.infinitepower.org/images/color12.gif" \* MERGEFORMATINET ����
6.0 - 6.5�
7,880 - 8,540�
1.9 - 2.1�
�
� INCLUDEPICTURE "http://www.infinitepower.org/images/color13.gif" \* MERGEFORMATINET ����
6.5 - 7.0�
8,540 - 9,200�
2.1 - 2.3�
�
� INCLUDEPICTURE "http://www.infinitepower.org/images/cloor14.gif" \* MERGEFORMATINET ����
>7.0�
>9,200�
>2.3�
�













































Page 1 of 32

[image: image135.png]


[image: image136.jpg]6 amp

ouTPUT

DC AMPERES

Simpica




[image: image137.jpg]PDowN), O-25.52

SOLAR TESTER AP, 2558

e —



[image: image138.png]£




[image: image139.png]I gencral,sunshine ncreases

rather uniormiy wih distance

Desert regons ofFar West from the GuifCoast

Toxas contai the suniest

areas i the stat a5 el ™

25 some ofthe sunlest 1
“nenaton.

i

e (5 hcstions i Toras Pty .




[image: image140.png]


[image: image141.png]


[image: image142.png]


[image: image143.png]


[image: image144.png]


[image: image145.png]


[image: image146.png]


[image: image147.png]


[image: image148.png]


[image: image149.png]


[image: image150.bmp][image: image151.png]- Read Solar Radiation Data Sigle Day Analyss Notes -The program passes information
path | Procecd WibhoutloggerDate | | Clocksuse  CodkSumset | i ey i perfoms the
EETET B
— File Names (1 minute data spacing only) Decimal Sunrise  Decimal Sunset
oo e Epectd i per tled ki of s
 Tovan sousrder iz S
" SARAGOSA_SOLAR.dat Cearsky [
Insert Year and Day (001 for Jan. T L
' 273 for Sept. 30, etc.) f— — ‘StartDay ‘Stop Day.
o z
= [ s
i)

ol

[
oo Sweep Panel Angies
Tit Start TitStop - TitStepsize -Deg | I
0 ) s o O |
Azmuth Start Azmuth Stop — Admith Stepsize -Deg —
E) m Cs6n Cs I
RUN SWEEP. i

Last Two Lines Read from Solar Radiation Data Fle:




[image: image152.jpg]1. For faster sweep execution, minimize the screen hide the graphs. 1-minute data | Tracking Method Meas. GH Clear Sky PA | PA Calc. Method 1] Meas. PA
2. Is best to not re-save this spreadsheet in case you have accidently only 0= None kWH/m2 KWH/m2 KWH/m2 KWH/m2
changed some of the cells that contain imbedded instructions or formulas. Loop Timer 1= Single Axis One Day One Day One Day One Day
4:53:47 PM 2 = Tilt Only 3.71 6.35 4.53 0.00
Measurement [Measurement an
and Panel Panel Longitude Panel Tilt Clear Sky GH
Day of Year Latitude Shift Panel Tilt | Panel Az. Sweep | Panel Az Sweep| 3 = Sun Following One Day
5 4.06
olar time Sunrise | ounset | sunrise Solar Noon
Sun declination] Equation of correction Hours of (clock (clock (decimal Sunrise (decimal clock Solar Noon
angle time (mins) (hours) sun time) time) hour) | (decimal hour) time) (clock time)
Incident
Angle for
-10.66 -0.65 10.22 0732 1746 7.53 17.77 12.65 1239 Sun this
Clear Sky Comparison for Panel, Lat. 31.55, Long. Shift -7.11 Tracking
o Cloar Sky = 6.35 KAH/M2, =mmmmMeas, PA  emmmMeas. GH Solar Measurements, File BAYLOR_SOLAR.dat
Method
1200 e GH e DH s PA —— GHX.
1000 2 1200 Clear Sky
i ' [—we
rd \ 1200
E 600 / 8
N & 1000
400 \ § o0
800
400
200 o
E 600
200 s
" . | H
5 6 7 8 9 10 11 12 13 14 15 16 17 18 19 20 0 7 400
Year 2013, Day 19, Tilt 30, Azimuth 180 5 6 7 8 9 10 11 12 13 14 15 16 17 18 19 20 200
Year 2013, Day 19
0 12 0.200 0452 186776  -0.976 YT




[image: image153.jpg]1. For faster sweep execution, minimize the screen hide the graphs. 1-minute data | Tracking Method Meas. GH Clear Sky PA | PA Calc. Method 1] Meas. PA
2. Is best to not re-save this spreadsheet in case you have accidently only 0= None kWH/m2 KWH/m2 KWH/m2 KWH/m2
changed some of the cells that contain imbedded instructions or formulas. Loop Timer 1= Single Axis One Day One Day One Day One Day
2:06:53 PM 2 = Tilt Only 5.21 6.37 741 0.00
Measurement [Measurement an
and Panel Panel Longitude Panel Tilt Clear Sky GH
Day of Year Latitude Shift Panel Tilt | Panel Az. Sweep | Panel Az Sweep| 3 = Sun Following One Day
9 4.09
olar time Sunrise | ounset | sunrise Solar Noon
Sun declination] Equation of correction Hours of (clock (clock (decimal Sunrise (decimal clock Solar Noon
angle time (mins) (hours) sun time) time) hour) | (decimal hour) time) (clock time)
Incident
Angle for
-10.96 -0.66 10.23 0732 1747 7.53 17.78 12.66 1239 Sun this
Clear Sky Comparison for Panel, Lat. 31.55, Long. Shift -7.11 Tracking
— Cloar Sky = 6.37 KAH/M2, =mmmMeas, PA  emmmMeas. GH Solar Measurements, File BAYLOR_SOLAR.dat
Method
1200 e GH e DH s PA —— GHX.
Clear Sky
000 1200 ear Sky
lear S| 5
5 ‘\‘ 1000 lear Sky
\ . 1200
E 600 Y
\ o / 1000
00 \ § 600 4
/ 800
400
200 /I g 00
200 s
. ! H
5 6 7 8 9 10 11 12 13 14 15 16 17 18 19 20 0 ; 400
Year 2013, Day 20, Tilt 30, Azimuth 180 5 6 7 8 9 10 11 12 13 14 15 16 17 18 19 20 200
Year 2013, Day 20
12 0.200 0457 186.851 -0.975 YT



[image: image154.jpg]1. For faster sweep execution, minimize the screen hide the graphs.

1-minute data | Tracking Method Meas. GH Clear Sky PA

PA Calc. Method 1

Meas. PA

12 0.200 -0.904 193.564

2. Is best to not re-save this spreadsheet in case you have accidently only 0= None kWH/m2 KWH/m2 KWH/m2
changed some of the cells that contain imbedded instructions or formulas. Loop Timer 1= Single Axis One Day One Day One Day
2:15:36 PM 2= Tit Only 4.48 6.94 7.29
Measurement [Measurement an
and Panel Panel Longitude Clear Sky GH
Latitude Shift Panel Tilt | Panel Az. Panel Az Sweep| 3 = Sun Following One Day
_ 4.17
olar time Sunrise | ounset Solar Noon
Sun declination] Equation of correction Hours of (clock (clock Sunrise (decimal clock Solar Noon
time (mins) (hours) sun time) (decimal hour) time) (clock time)
Incident
Angle for
-11.54 -1.10 10.30 0757 18.25 13.10 1306 this
Clear Sky Comparison for Panel, Lat. 31.35, Long. Shift -13.68 Tracking
e Cloar Sky = 8.43 KAH/M2, =mmmMeas, PA  emmmMeas. GH Solar Measurements, File TOYAH_SOLAR.dat
‘ Method
T —Y —GHX‘
j— 1200 Clear Sky F
P s
// 1000 r e lear Sky =64
/ N 1200
y./ AW = 800 N
o \ 1000
\ 600 i
/ \ 800
/i \ 400
200 \ 600
8§ 9 10 11 12 13 14 15 16 17 18 19 20 o 400
Year 2013, Day 22, Tilt 30, Azimuth 180 5 6 7 8 9 10 11 12 13 14 15 16 17 18 00
Year 2013, Day 22
0
5 6



[image: image155.jpg]1. For faster sweep execution, minimize the screen hide the graphs. 1-minute data | Tracking Method Meas. GH Clear Sky PA | PA Calc. Method 1] Meas. PA
2. Is best to not re-save this spreadsheet in case you have accidently only 0= None kWH/m2 KWH/m2 KWH/m2 KWH/m2
changed some of the cells that contain imbedded instructions or formulas. Loop Timer 1= Single Axis One Day One Day One Day One Day
2:10:18 PM 2 = Tilt Only 3.55 6.08 5.13 5.56
Measurement [Measurement an
and Panel Panel Longitude Panel Tilt Clear Sky GH
Day of Year Latitude Shift Panel Tilt | Panel Az. Sweep | Panel Az Sweep] 3 = Sun Following One Day
_ 3.74
olar time Sunrise | ounset | Sunrise Solar Noon
Sun declination] Equation of correction Hours of (clock (clock (decimal Sunrise (decimal clock Solar Noon
angle time (mins) (hours) sun time) time) hour) | (decimal hour) time) (clock time)
Incident
Angle for
-3.71 -0.97 10.00 0758 1758 7.97 17.97 12.97 1258 Sun this
Clear Sky Comparison for Panel, Lat. 31.35, Long. Shift -13.68 Tracking
o Cloar Sky = 6.08 KAH/M2, emmmmMeas, PA  emmmMeas. GH Solar Measurements, File TOYAH_SOLAR.dat
Method
1200 e GH e DH s PA —— GHX
Clear Sky F
1000 1200 ear Sky
. 1000 lear Sky = 6.0
1200
E 600 &
o 1000
400 § 600
\ 400 &0
200 \ o
E 600
200 s
0 H
5 6 7 8 9 10 11 12 13 14 15 16 17 18 19 20 o | 400
Year 2013, Day 1, Tilt 30, Azimuth 180 5 6 7 8 9 10 11 12 13 14 15 16 17 18 19 20 200
Year 2013, Day 1
12 0.200 0774 191606 -0.973 LYo s



[image: image156.png]T 7 Solar_Data Analyzer 130124xism - Microsoft Excel =
Home  Inset  Pagelayout  Fomulas  Data  Review  View  Auobat  Team
E] @ -
[z0) - £ | Degrees
A B & D | E | F G H 1 J K L M N o P Q R 5 =
1 - 1. For faster sweep execution, minimize the screen hide the graphs. A.minute data | Tracking Method | Meas.GH |Clear Sky PA|PA Calc. Method 1| Meas. PA Clear Sky Clear Sky Clear Sky  Clear Sky=|
2 2.15 best to not re-save this spreadsheet in case you have accidently only 0=None kwim2 | kwim2 KWHIm2 KWHm2 Daily Sun Apparent Optical Difuse
3 [changed some of the cells that contain imbedded instructions or formulas. | Loop Timer | 1=SingleAis [ OneDay | OneDay One Day One Day 12 flours Exterrest  Depth Factor C
4 45347PM_|_2=TitOnly 371 635 453 000 FlucA
Weasurement | Measurement 10
anaPanel | - andPanel PanelTit [ Panel a2 Clear Sky GH Masters Masters Eq Masters Eq Master's E
5 Latitude | Longitude Shift Panel Tilt Sweep. Sweep  [3=Sun Following| _One Day 8 Eq(722) (123) (721) (7.28)
s o ——r— . un
7 pr Sky[ 160
Sunise "Sofar Noon A Prto PR
Equation of (decimal |  Sunise | (decimal clock | Solar Noon ters  Variation
8 ange | time(mins) | (hours) sun | time) | time) | hou) [(decimalhou)| time) (clock time) 2 [ K1 ct
Incident
Anglefor | 0 Beam
9 205 1066 065 102 | or2 | 1ms | 783 1777 1265 1239 Sun this Reaching 3
1€ < V1 Main Sheet . %3 8 Ml ] v
Ready | E@@ w00% C 0 +




_1218862074.unknown

_1345820016.unknown

_1397968281.unknown

_1397968558.unknown

_1397968846.unknown

_1397968855.unknown

_1397968579.unknown

_1397968756.unknown

_1397968571.unknown

_1397968427.unknown

_1397968436.unknown

_1397968466.unknown

_1397968301.unknown

_1347081443.unknown

_1397968063.unknown

_1397968152.unknown

_1397968243.unknown

_1397968115.unknown

_1397967756.unknown

_1397967785.unknown

_1347253695.unknown

_1397967595.unknown

_1347253694.unknown

_1347253693.unknown

_1346470757.unknown

_1346472231.unknown

_1346474080.unknown

_1346474346.unknown

_1346472806.unknown

_1346473260.unknown

_1346473730.unknown

_1346473250.unknown

_1346472469.unknown

_1346471531.unknown

_1346472012.unknown

_1346471044.unknown

_1345860561.unknown

_1346470748.unknown

_1345820104.unknown

_1345803243.unknown

_1345812648.unknown

_1345816602.unknown

_1345816836.unknown

_1345812953.unknown

_1345803448.unknown

_1345804372.unknown

_1345804421.unknown

_1345803683.unknown

_1345803734.unknown

_1345803797.unknown

_1345803721.unknown

_1345803610.unknown

_1345803288.unknown

_1345803310.unknown

_1345803260.unknown

_1345799743.unknown

_1345799821.unknown

_1345799925.unknown

_1345800008.unknown

_1345799805.unknown

_1218862818.unknown

_1284894691.unknown

_1284894701.unknown

_1218862831.unknown

_1218862543.unknown

_1190790353.unknown

_1196829989.unknown

_1196930325.unknown

_1196945535.unknown

_1196945730.unknown

_1196950720.unknown

_1196950811.unknown

_1196946449.unknown

_1196945552.unknown

_1196930768.unknown

_1196830646.unknown

_1196930277.unknown

_1196830685.unknown

_1196830102.unknown

_1196830341.unknown

_1196827957.unknown

_1196828840.unknown

_1196829466.unknown

_1196829941.unknown

_1196829747.unknown

_1196829322.unknown

_1196829363.unknown

_1196827991.unknown

_1196828054.unknown

_1196827387.unknown

_1196827935.unknown

_1190790365.unknown

_1190440185.unknown

_1190789880.unknown

_1190790228.unknown

_1190790301.unknown

_1190789909.unknown

_1190789972.unknown

_1190788047.unknown

_1190788701.unknown

_1190788090.unknown

_1190440779.unknown

_1190440789.unknown

_1190787997.unknown

_1190440236.unknown

_1168012647.unknown

_1179471941.unknown

_1179472492.unknown

_1190440118.unknown

_1179472048.unknown

_1179463462.unknown

_1179471892.unknown

_1168012382.unknown

_1168012414.unknown

_1066588929.unknown

_1150136746.unknown

_1066581521.unknown

