_07_ELC4340_Spring13_Per_Unit_System.doc

1.
Single-Phase Per Unit System

Advantages of the per unit system:

1.
Transformers can be replaced by their equivalent series impedances.

2.
Equipment impedances can be easily estimated since their per unit impedances lie within a relatively narrow range.

Define four quantities in per unit of their respective base values:


[image: image1.wmf]volts

volts

V

V

V

base

pu

=

 ,


[image: image2.wmf]amps

amps

I

I

I

base

pu

=

 ,


[image: image3.wmf]voltamps

voltamps

S

S

S

base

pu

=

 ,

[image: image4.wmf]ohms

ohms

Z

Z

Z

base

pu

=

 .

The relationships among the bases are



[image: image5.wmf]base

base

base

I

V

S

·

=

 , and 
[image: image6.wmf]base

base

base

I

V

Z

=

 .

Once two base variables are specified, the other two base variables may be calculated.

A convenient relation, derived from the two above equations, is



[image: image7.wmf]base

base

base

base

base

base

base

base

Z

V

Z

V

V

I

V

S

2

=

·

=

·

=

 .

Consider a transformer with an 
[image: image8.wmf]2

1

:

N

N

 turns ratio and series impedance, reflected on side 1, equal 
[image: image9.wmf]1

L

Z

 .  
[image: image10.wmf]1

L

Z

 can be reflected to side 2 using



[image: image11.wmf]1

2

1

2

2

L

L

Z

N

N

Z

ú

û

ù

ê

ë

é

=

 .

Let side 1 and side 2 have base values designated by subscripts S1 and S2.  Then



[image: image12.wmf]1

2

1

1

base

base

base

S

V

Z

=

 ,


[image: image13.wmf]2

2

2

2

base

base

base

S

V

Z

=

 ,

Expressing the transformer impedance on the two respective bases yields



[image: image14.wmf]2

1

1

1

1

base

base

L

PU

L

V

S

Z

Z

=

 , 

[image: image15.wmf]2

2

2

2

2

base

base

L

PU

L

V

S

Z

Z

=

 .

If 
[image: image16.wmf]2

1

B

B

S

S

=

 , the two above equations may be combined so that



[image: image17.wmf]PU

L

base

base

PU

L

Z

V

V

N

N

Z

1

2

2

1

2

1

2

2

ú

û

ù

ê

ë

é

ú

û

ù

ê

ë

é

=

 .

Substituting the relation between 
[image: image18.wmf]1

L

Z

 and 
[image: image19.wmf]2

L

Z

 yields



[image: image20.wmf]PU

L

base

base

PU

L

Z

V

V

N

N

Z

1

2

2

1

2

1

2

2

ú

û

ù

ê

ë

é

ú

û

ù

ê

ë

é

=

 .

Therefore, if 
[image: image21.wmf]1

2

1

2

N

N

V

V

base

base

=

 , then 
[image: image22.wmf]PU

L

PU

L

Z

Z

1

2

=

 .

Hence, if a common voltampere base is chosen on both sides of the transformer, and if the voltage bases are chosen so that they vary according to the transformer turns ratio, then the per unit series impedance of the transformer is the same value on both sides.

When analyzing a circuit with many transformers, a common voltampere base should be chosen throughout the circuit, and a voltage base should be chosen at one location.  The voltage base must vary across the circuit according to the transformer turns ratios.

When analyzing a circuit in per unit, if the bases are chosen according to the above rules, transformers can be replaced by their equivalent per unit series impedances, and their turns can be ignored.

A manufacturer usually provides the impedance of a transformer on the transformer's rated voltage and power bases.  However, when solving a power network circuit, the power and voltage bases must vary according to the above rules, and they may not equal the manufacturer-specified bases.  Per unit impedances, specified on one base, may be converted to a new base as follows:

Given 
[image: image23.wmf]old

base

old

PU

Z

Z

Z

,

,

=

 , on bases 
[image: image24.wmf]old

base

V

,

 and 
[image: image25.wmf]old

base

S

,

 , 
[image: image26.wmf]new

PU

Z

,

 on new bases 
[image: image27.wmf]new

base

V

,

 and 
[image: image28.wmf]new

base

S

,

 is



[image: image29.wmf]ú

ú

û

ù

ê

ê

ë

é

ú

ú

û

ù

ê

ê

ë

é

=

=

=

2

,

,

,

2

,

,

,

,

,

,

,

new

base

new

base

old

base

old

base

old

PU

new

base

old

base

old

PU

new

base

ohms

new

PU

V

S

S

V

Z

Z

Z

Z

Z

Z

Z

 .

2.
Three-Phase Per Unit System

The same advantages apply to a three-phase system if the following rules are obeyed:

1.
A common three-phase voltampere base is used throughout the system, where




[image: image30.wmf]F

F

=

1

,

3

,

3

base

base

S

S

 .

2.
Once selected at a point in the network, the three-phase voltage base must vary according to the line-to-line transformer turns ratios.

Convenient formulas relating single-phase to three-phase bases are given below.



[image: image31.wmf]base

neutral

line

base

base

I

V

S

·

=

-

,

1

,

f

 ,



[image: image32.wmf]f

f

1

,

3

,

3

base

base

S

S

=

 ,



[image: image33.wmf][

]

f

f

f

3

,

2

,

3

,

,

2

1

,

2

,

3

/

3

/

base

line

line

base

base

line

line

base

base

neutral

line

base

base

S

V

S

V

S

V

Z

-

-

-

=

=

=

 .

Example Problem:

Information for a small power system is shown below.  Per unit values are given on the equipment bases.  Using a 138kV, 100MVA base in the transmission lines, draw the positive and negative sequence per unit diagrams.  Assume that no current is flowing in the network, so that all generator and motor voltages are 1.0pu (positive sequence) in your final diagram.





 
#4





#1





#3





#5





Trans3


X = 0.10


40MVA


138kV GY/ 13.8kV Delta





Trans3





TLine2





Trans2





TLine1





Trans1


X = 0.16


60MVA


138kV GY/ 18kV Delta





Trans1





#2





#6





Gen1


X” = 0.15


40MVA


20kV GY,


j0.1 ohm grounding reactor





Line1


R+ = 10Ω


X+ = 60Ω





Line2


R+ = 10Ω


X+ = 60Ω





Motor


X” = 0.10


25MVA


13.2kV


Delta





Trans2


X=0.14


50MVA


138kV GY/ 20kV Delta





For transmission lines, assume that


R0 = 5 • R+


X0 = 3 • X+





For generators and transformers, 


let Z0 = Z+





Negative seq. impedances same as positive seq. impedances.





Gen2, X” = 0.15, 35MVA, 22kVGY, j0.1 ohm grounding reactor








Page 1 of 3

_1209964048

_1209964079

_1209964092

_1209964108

_1209964114

_1209964121

_1209964220.unknown

_1209964221.unknown

_1209964219.unknown

_1209964117

_1209964111

_1209964103

_1209964106

_1209964100

_1209964086.unknown

_1209964089

_1209964083

_1209964061

_1209964073

_1209964075.unknown

_1209964070

_1209964055

_1209964058

_1209964051

_1209964037

_1209964042

_1209964045

_1209964039

_970749445

_1209964033

_970749438

_970749442

_970749420

