_18_ELC4340_Spring13_Loadflow.doc 

Loadflow

Formulation of the loadflow problem.  Gauss-Seidel, Newton-Raphson, and Stott's algorithm.  Calculation of line flows, system losses, and area interchange.

1
Formulation of the Problem

The loadflow problem is one of the classic power system engineering problems.  During the early days of digital computers, many advances in techniques for solving large sets of equations were brought about specifically to help solve the loadflow problem.

In most electrical circuit analyses, the network consists of known impedances, voltage sources, and current sources.  However, in the loadflow problem, active and reactive powers, rather than shunt impedances, are specified at most network busses, because most loads behave, on average, as constant power loads (active and reactive power), as long as their applied voltage remains within reasonable ranges.  Consider, for example, the air conditioning load of a building.  A certain amount of energy is required to maintain 
[image: image1.wmf]D

T

 between inside and outside temperatures.  Even though the air conditioner cycles on-and-off, and the voltage may change slightly, the air conditioning load appears, on the average, as a fixed power load, rather than as a fixed impedance load.

Power system loads are closely monitored at substations, at large customers, and for total electric utility companies.  Loads tend to have predictable daily, weekly, and seasonal patterns.  Annual peak demands and energies for electric utilities are forecasted for generation and planning purposes. 

Most loadflows model three-phase balanced systems.  Positive-sequence values, usually in per unit, represent R, L, C, P, Q, S, Ω, V, and I.  

The purpose of the loadflow program is to compute bus voltages and line/transformer/cable power flows once network topology, impedances, loads, and generators have been specified.  Ideally, the computed bus voltages for the study system should remain within acceptable ranges, and line/transformer/cable power flows should be below their rated values, for a reasonable set of outage contingencies.

From a loadflow perspective, there are four parameters at every bus - voltage magnitude V, voltage angle 
[image: image2.wmf]d

, active power P, and reactive power Q.  Two may be specified, and the other two calculated.  For most busses, P and Q are specified, and V and 
[image: image3.wmf]d

 are calculated.  Obviously, P and Q cannot be specified at all busses because that would imply that system losses are known a priori.  Therefore, the loadflow problem must include one "swing bus" at which the P can assume any value so that it "makes up" system losses.  The swing bus is usually a centrally-located large generator whose voltage magnitude and phase angle (usually 
[image: image4.wmf]d

 = zero) are specified.

Although any two of the four parameters can be specified, the usual way in which power system busses are classified is given in Table 1.

Table 1.  Loadflow Classification of Power System Busses

	Classification
	Knowns
	Unknowns

	PQ (Load Bus)
	P, Q
	V, 
[image: image5.wmf]d



	PV (Generator Bus)
	P, V
	Q, 
[image: image6.wmf]d



	V
[image: image7.wmf]d

 (Swing Bus)
	V, 
[image: image8.wmf]d


	P, Q


The loadflow program solves for the set of unknowns that produces power balance at all busses, or as illustrated for bus i in Figure 1,



[image: image9.wmf]calc

i

calc

i

spec

i

spec

i

jQ

P

jQ

P

+

=

+

 ,

where



[image: image10.wmf]*

i

i

calc

i

calc

i

I

V

jQ

P

=

+

 .

In other words, the power specified at each bus must equal the power flowing into the system.  Note in Figure 1 that specified power is drawn as positive generation, to be consistent with KCL equation YV=I.


[image: image11.wmf]Total Current Flowing From Bus i into the System is

P  +  jQ

i

i

spec

spec

IB1

IB2

IB3

Bus i

Branch

Currents

Into

System

I  = IB1 + IB2 + IB3

i

= V  I

i

i

*

V

i

i

d

|

|


Figure 1.  Power Balance for Bus i
Since there are two unknowns at every bus, the size of the loadflow problem is 2N, where N is the number of busses.  Obviously, to solve the problem, there must be two equations for every bus.  These come from KCL, which for any bus i have the form 



[image: image12.wmf]*

1

,

*

ú

ú

û

ù

ê

ê

ë

é

=

=

+

=

+

å

=

N

j

j

j

i

i

i

i

calc

i

calc

i

spec

i

spec

i

V

y

V

I

V

jQ

P

jQ

P

 .

Separating into real and imaginary components yields two equations for bus i,



[image: image13.wmf](

)

j

i

j

i

j

j

i

N

j

i

spec

i

V

y

V

P

,

,

1

cos

q

d

d

-

-

=

å

=

 ,



[image: image14.wmf](

)

j

i

j

i

j

j

i

N

j

i

spec

i

V

y

V

Q

,

,

1

sin

q

d

d

-

-

=

å

=

 ,

where 
[image: image15.wmf]j

i

j

i

j

i

j

j

j

i

i

i

y

y

V

V

V

V

,

,

,

 

,

 

 

,

 

q

d

d

Ð

=

Ð

=

Ð

=

 .

The problem now is now to find the set of bus voltages that satisfies the above 2N equations.

2.
Gauss-Seidel Method

Gauss-Seidel is an early formulation of the loadflow problem that requires little memory and it is easily programmed.  However, it is usually slower than other methods.  It is based upon the idea of expanding the complex form of the power balance equation as follows:



[image: image16.wmf]*

,

1

,

,

*

1

,

*

ú

ú

û

ù

ê

ê

ë

é

+

=

ú

ú

û

ù

ê

ê

ë

é

=

=

+

å

å

¹

=

=

N

i

j

j

j

j

i

i

i

i

i

N

j

j

j

i

i

i

i

spec

i

spec

i

V

y

V

y

V

V

y

V

I

V

jQ

P

 ,

or



[image: image17.wmf]å

¹

=

+

=

-

N

i

j

j

j

j

i

i

i

i

i

i

spec

i

spec

i

V

y

V

V

y

V

jQ

P

,

1

,

*

,

*

 ,

so that



[image: image18.wmf]ú

ú

û

ù

ê

ê

ë

é

-

-

=

å

¹

=

N

i

j

j

j

j

i

i

spec

i

spec

i

i

i

i

V

y

V

jQ

P

y

V

,

1

,

*

,

1

 .

The solution procedure is to:

1.
Initialize the bus voltages.  For load busses, use V = 1 + j0.  For generator busses (including the swing bus), use 
[image: image19.wmf]0

j

V

V

spec

+

=

.

2.
One-by-one, update the individual bus voltages using 

[image: image20.wmf]ú

ú

û

ù

ê

ê

ë

é

-

-

=

å

¹

=

N

i

j

j

j

j

i

i

spec

i

spec

i

i

i

i

V

y

V

jQ

P

y

V

,

1

,

*

,

1

.


For PV busses, update the voltage angle, while holding the voltage magnitude constant at the specified value.  Do not update the swing bus.

3.
Check the mismatch P and Q at each bus.  If all are within tolerance (typical tolerance is 0.00001 pu), a solution has been found.  Otherwise, return to Step 2.

Convergence is usually faster if an acceleration factor is used.  For example, assume that the voltage at bus i at iteration m is 
[image: image21.wmf]m

i

V

 , and that the updating equation in Step 2 computes 
[image: image22.wmf]new

j

V

 .  Instead of using 
[image: image23.wmf]new

j

V

 directly, accelerate the update with



[image: image24.wmf](

)

m

i

new

i

m

i

m

i

V

V

V

V

-

+

=

+

a

1

,

where acceleration factor 
[image: image25.wmf]a

 is in the range of 1.2 to 1.6.

3
Newton-Raphson Method

The Newton-Raphson method is a very powerful loadflow solution technique that incorporates first-derivative information when computing voltage updates.  Normally, only 3 to 5 iterations are required to solve the loadflow problem, regardless of system size.  Newton-Raphson is the most commonly used loadflow solution technique.

An easy way to illustrate the Newton-Raphson technique is to solve a simple equation whose answers are already known.  For example, consider



[image: image26.wmf](

)

(

)

0

99

1

=

-

-

x

x

,

which when expanded becomes



[image: image27.wmf]0

99

100

2

=

+

-

x

x

.

The objective is to find x so that



[image: image28.wmf]0

99

100

)

(

2

=

+

-

=

x

x

x

f

.

Of course, in this case, the two solutions are known a priori as  x = 1, and x = 99.

The Newton-Raphson procedure is based on Taylor's expansion, truncated past the first derivative, which gives



[image: image29.wmf](

)

x

x

x

f

x

f

x

x

f

x

D

+

»

D

+

¶

¶

)

(

)

(

)

(

 .

Clearly, the above equation gives a straight-line approximation for 
[image: image30.wmf])

(

x

x

f

D

+

 .

The objective is to find 
[image: image31.wmf]x

D

 so that 
[image: image32.wmf])

(

x

x

f

D

+

 is the desired value (which in this example is zero).  Solving for 
[image: image33.wmf]x

D

 yields



[image: image34.wmf]x

x

x

f

x

f

x

x

f

x

¶

¶

)

(

)

(

)

(

-

D

+

=

D

 ,

which for this example is



[image: image35.wmf]x

x

x

x

f

x

f

x

x

f

x

f

x

¶

¶

¶

¶

)

(

)

(

)

(

)

(

0

-

=

-

=

D

 .

The update equation for iteration (m + 1) is then



[image: image36.wmf])

(

)

(

)

(

)

(

)

1

(

)

(

)

(

m

x

m

m

m

m

x

x

f

x

f

x

x

x

x

¶

¶

-

=

D

+

=

+

 ,

where in this example



[image: image37.wmf]100

2

)

(

-

=

x

x

x

f

¶

¶

 .

If a starting point of x = 2 is chosen, then the solution proceeds as follows:


Iteration - m
x
f(x)

[image: image38.wmf]x

x

f

¶

¶

)

(



0
2
-97
-96


1
0.9896
1.0193
-98.02


2
0.9999
0.0098
-98.00

Additional iterations can be performed if tighter solution tolerance is needed.  Note that if a starting point of x = 50 had been chosen, the partial derivative would have been zero, and the method would have failed.

If x = 80 is the starting point, then the process yields the following:


Iteration - m
x
f(x)

[image: image39.wmf]x

x

f

¶

¶

)

(



0
80
-1501
60


1
105.02
626.2
110.04


2
99.33
32.45
98.66


3
99.00
0
98.00

Therefore, the starting point greatly affects the ability of a Newton-Raphson method to converge, and the answer to which it converges.  Fortunately, in the loadflow problem, most voltages are near 1.0 pu in magnitude and 0.0 degrees, so that we are able to accurately estimate starting values.

For the loadflow problem, the Newton-Raphson method is expanded in matrix form.  For example, consider a set of N nonlinear equations and N unknowns,



[image: image40.wmf](

)

(

)

(

)

N

N

N

N

N

y

x

x

x

f

y

x

x

x

f

y

x

x

x

f

=

=

=

,

,

,

,

,

,

,

,

,

2

1

2

2

1

2

1

2

1

1

L

M

M

M

L

L

 .

The task is to find the set of unknown 
[image: image41.wmf]N

x

x

x

,

,

,

2

1

L

 , given the known set 
[image: image42.wmf]N

y

y

y

,

,

,

2

1

L

, and given a starting point 
[image: image43.wmf])

0

(

)

0

(

2

)

0

(

1

,

,

,

N

x

x

x

L

 .

Applying Taylor's theorem as before, truncated after the first derivative, yields for Row i


[image: image44.wmf](

)

=

D

+

D

+

D

+

»

N

N

i

i

x

x

x

x

x

x

f

y

)

0

(

2

)

0

(

2

1

)

0

(

1

,

,

,

L

 
[image: image45.wmf](

)

+

)

0

(

)

0

(

2

)

0

(

1

,

,

,

N

i

x

x

x

f

L




+ 
[image: image46.wmf])

0

(

)

0

(

2

2

)

0

(

1

1

x

N

i

N

x

i

x

i

x

f

x

x

f

x

x

f

x

¶

¶

¶

¶

¶

¶

D

+

+

D

+

D

L

 ,

where x(0) represents the starting estimate set 
[image: image47.wmf])

0

(

)

0

(

2

)

0

(

1

,

,

,

N

x

x

x

L

 .

N similar equations in matrix form are



[image: image48.wmf](

)

(

)

(

)

ú

ú

ú

ú

ú

û

ù

ê

ê

ê

ê

ê

ë

é

+

ú

ú

ú

ú

û

ù

ê

ê

ê

ê

ë

é

D

D

D

ú

ú

ú

ú

ú

ú

ú

ú

û

ù

ê

ê

ê

ê

ê

ê

ê

ê

ë

é

»

ú

ú

ú

ú

û

ù

ê

ê

ê

ê

ë

é

)

0

(

)

0

(

2

)

0

(

1

)

0

(

)

0

(

2

)

0

(

1

2

)

0

(

)

0

(

2

)

0

(

1

1

2

1

2

1

2

2

2

1

2

1

2

1

1

1

2

1

,

,

,

,

,

,

,

,

,

N

N

N

N

N

N

N

N

N

N

N

N

x

x

x

f

x

x

x

f

x

x

x

f

x

x

x

x

f

x

f

x

f

x

f

x

f

x

f

x

f

x

f

x

f

y

y

y

L

M

L

L

M

L

M

M

M

L

L

M

¶

¶

¶

¶

¶

¶

¶

¶

¶

¶

¶

¶

¶

¶

¶

¶

¶

¶

 ,

or



[image: image49.wmf](

)

(

)

(

)

[

]

ú

ú

ú

ú

û

ù

ê

ê

ê

ê

ë

é

D

D

D

»

ú

ú

ú

ú

ú

û

ù

ê

ê

ê

ê

ê

ë

é

-

-

-

N

N

N

N

N

N

x

x

x

J

x

x

x

f

y

x

x

x

f

y

x

x

x

f

y

M

L

M

L

L

2

1

)

0

(

)

0

(

2

)

0

(

1

)

0

(

)

0

(

2

)

0

(

1

2

2

)

0

(

)

0

(

2

)

0

(

1

1

1

 

,

,

,

,

,

,

,

,

,

 ,

where J is an N x N matrix of partial derivatives, known as the Jacobian matrix.  Therefore, in an iterative procedure, the above equation is used to update the X vector according to



[image: image50.wmf][

]

[

]

)

(

1

)

(

)

(

)

(

)

(

)

1

(

m

spec

m

m

m

m

m

Y

Y

J

X

X

X

X

-

+

=

D

+

=

-

+

 ,

where



[image: image51.wmf](

)

(

)

(

)

ú

ú

ú

ú

ú

û

ù

ê

ê

ê

ê

ê

ë

é

=

ú

ú

ú

ú

û

ù

ê

ê

ê

ê

ë

é

=

)

(

)

(

2

)

(

1

)

(

)

(

2

)

(

1

2

)

(

)

(

2

)

(

1

1

)

(

2

1

,

,

,

,

,

,

,

,

,

 

,

 

m

N

m

m

N

m

N

m

m

m

N

m

m

m

N

spec

x

x

x

f

x

x

x

f

x

x

x

f

Y

y

y

y

Y

L

M

L

L

M

 .

In the loadflow problem, the matrix update equation is symbolically written in mixed rectangular-polar form as



[image: image52.wmf](

)

(

)

(

)

(

)

(

)

(

)

(

)

(

)

(

)

(

)

(

)

(

)

(

)

(

)

(

)

(

)

(

)

(

)

ú

ú

ú

ú

ú

ú

ú

ú

ú

ú

ú

ú

ú

û

ù

ê

ê

ê

ê

ê

ê

ê

ê

ê

ê

ê

ê

ê

ë

é

-

-

-

-

-

-

-

-

-

ú

ú

ú

ú

û

ù

ê

ê

ê

ê

ë

é

=

=

=

=

=

ú

ú

ú

ú

ú

ú

ú

ú

ú

ú

ú

ú

ú

û

ù

ê

ê

ê

ê

ê

ê

ê

ê

ê

ê

ê

ê

ê

ë

é

-

-

-

-

-

-

-

-

-

+

+

+

+

+

+

m

N

m

N

m

m

m

m

m

N

m

N

m

m

m

m

m

Ncalc

Nspec

m

calc

spec

m

calc

spec

m

Ncalc

Nspec

m

calc

spec

m

calc

spec

V

V

V

V

V

V

V

Q

J

Q

J

V

P

J

P

J

Q

Q

Q

Q

Q

Q

P

P

P

P

P

P

1

2

1

2

1

1

1

1

2

1

2

1

1

1

4

3

2

1

)

(

)

(

2

2

)

(

1

1

)

(

)

(

2

2

)

(

1

1

M

M

M

M

d

d

d

d

d

d

¶

¶

¶d

¶

¶

¶

¶d

¶


or, in abbreviated form,



[image: image53.wmf]ú

û

ù

ê

ë

é

D

D

ú

û

ù

ê

ë

é

=

ú

û

ù

ê

ë

é

D

D

V

J

J

J

J

Q

P

d

4

3

2

1

 .

The dimension of the above problem is actually 
[image: image54.wmf](

)

(

)

2

busses

 

PV

 

of

Number 

2

-

-

N

 since 
[image: image55.wmf]V

 updates at PV busses are not required, and since 
[image: image56.wmf]V

 and 
[image: image57.wmf]d

 updates at the swing bus are not required.

In highly inductive power systems, P is closely related to voltage angles, and Q is closely related to voltage magnitudes.  Therefore, in the above mixed rectangular-polar formulation, the terms in 
[image: image58.wmf]4

1

 

and

 

J

J

 tend to have larger magnitudes than those in 
[image: image59.wmf]3

2

 

and

 

J

J

.  This feature makes the Jacobian matrix more diagonally dominant, which improves robustness when Gaussian eliminating or LU decomposing J.

The above formulation of the Jacobian matrix is often modified to take advantage of symmetry in the partial derivatives.  This modification is



[image: image60.wmf]ú

û

ù

ê

ë

é

D

D

ú

ú

ú

ú

û

ù

ê

ê

ê

ê

ë

é

=

ú

û

ù

ê

ë

é

D

D

V

V

V

Q

Q

V

V

P

P

V

Q

P

d

¶

¶

¶d

¶

¶

¶

¶d

¶

1

1

 .

The partial derivatives are derived from



[image: image61.wmf](

)

j

i

j

i

j

j

i

N

j

i

calc

i

V

y

V

P

,

,

1

cos

q

d

d

-

-

=

å

=

 ,



[image: image62.wmf](

)

j

i

j

i

j

j

i

N

j

i

calc

i

V

y

V

Q

,

,

1

sin

q

d

d

-

-

=

å

=

 ,

and have the following form


For 
[image: image63.wmf]1

J

 ,




[image: image64.wmf](

)

(

)

.

  

 

,

sin

sin

,

,

,

1

,

,

i

k

V

y

V

P

V

y

V

P

k

i

k

i

k

k

i

i

k

i

N

i

j

j

j

i

j

i

j

j

i

i

i

i

¹

-

-

=

-

-

-

=

å

¹

=

q

d

d

¶d

¶

q

d

d

¶d

¶



For 
[image: image65.wmf]2

J

 ,




[image: image66.wmf](

)

(

)

(

)

.

  

 

,

cos

cos

2

cos

,

,

,

,

1

,

,

,

i

k

y

V

V

P

y

V

V

y

V

P

k

i

k

i

k

i

i

k

i

i

i

N

i

j

j

i

i

i

j

i

j

i

j

j

i

i

i

¹

-

-

=

-

+

-

-

=

å

¹

=

q

d

d

¶

¶

q

q

d

d

¶

¶

 


For 
[image: image67.wmf]3

J

 ,




[image: image68.wmf](

)

(

)

.

  

 

,

cos

cos

,

,

,

1

,

,

i

k

V

y

V

Q

V

y

V

Q

k

i

k

i

k

k

i

i

k

i

N

i

j

j

j

i

j

i

j

j

i

i

i

i

¹

-

-

-

=

-

-

=

å

¹

=

q

d

d

¶d

¶

q

d

d

¶d

¶

 


For 
[image: image69.wmf]4

J

 ,




[image: image70.wmf](

)

(

)

(

)

.

  

 

,

sin

sin

2

sin

,

,

,

,

1

,

,

,

i

k

y

V

V

Q

y

V

V

y

V

Q

k

i

k

i

k

i

i

k

i

i

i

N

i

j

j

i

i

i

j

i

j

i

j

j

i

i

i

¹

-

-

=

-

+

-

-

=

å

¹

=

q

d

d

¶

¶

q

q

d

d

¶

¶

 

Note the symmetry in the J terms.  If 
[image: image71.wmf]d

V

 is used as an updating parameter rather than 
[image: image72.wmf]d

, then the expressions for 
[image: image73.wmf]1

J

 are




[image: image74.wmf](

)

(

)

.

  

 

,

sin

sin

,

,

,

1

,

,

i

k

y

V

V

P

V

y

V

P

k

i

k

i

k

i

i

k

k

i

N

i

j

j

j

i

j

i

j

j

i

i

i

i

¹

-

-

=

-

-

-

=

å

¹

=

q

d

d

¶d

¶

q

d

d

¶d

¶

 

and for 
[image: image75.wmf]3

J

 ,




[image: image76.wmf](

)

(

)

.

  

 

,

cos

cos

,

,

,

1

,

,

i

k

V

y

V

Q

V

y

V

Q

k

i

k

i

k

k

i

k

i

i

N

i

j

j

j

i

j

i

j

j

i

i

i

i

¹

-

-

-

=

-

-

=

å

¹

=

q

d

d

¶d

¶

q

d

d

¶d

¶

 

and there is even more symmetry in J.

The diagonal dominance of 
[image: image77.wmf]1

J

 and 
[image: image78.wmf]4

J

 can be observed by the examining the partial derivatives as follows:  the differences between voltage angles at adjacent busses is usually small, so that the 
[image: image79.wmf](

)

j

i

d

d

-

 terms are small.  The angles found in the admittance matrix are usually large (i.e. near 
[image: image80.wmf]o

90

) because most power systems are reactive.  Therefore, the sine terms in the matrix update equation tend to be near unity, while the cosine terms tend to be near zero.  Decoupled loadflow programs use only 
[image: image81.wmf]1

J

 and 
[image: image82.wmf]4

J

, treating the P and Q problems separately.

So that the benefits of optimal bus ordering can be fully exploited, non-decoupled loadflow Jacobian matrices are usually formulated in the following alternating-row form, rather than that described symbolically above:



[image: image83.wmf][

]

ú

ú

ú

ú

ú

ú

ú

ú

ú

û

ù

ê

ê

ê

ê

ê

ê

ê

ê

ê

ë

é

D

D

D

D

D

D

=

ú

ú

ú

ú

ú

ú

ú

ú

ú

û

ù

ê

ê

ê

ê

ê

ê

ê

ê

ê

ë

é

D

D

D

D

D

D

N

N

N

N

N

V

V

V

V

V

V

J

Q

P

Q

P

Q

P

d

d

d

M

M

2

2

2

1

1

1

2

2

1

1

 

 .

The solution procedure for the Newton-Raphson loadflow proceeds with:

1.
Initialize the bus voltages.  For load busses, use V = 1 + j0.  For generator busses (including the swing bus), use 
[image: image84.wmf]0

j

V

V

spec

+

=

.

2.
Form the Jacobian matrix, and update all bus voltage magnitudes and phase angles, except for those at the swing bus, and except for the voltage magnitudes at PV busses.

3.
Check the mismatch P and Q at each bus.  If all are within tolerance (typical tolerance is 0.00001 pu), a solution has been found.  Otherwise, return to Step 2.

4
Stott's Algorithm

Stott's algorithm takes advantage of the strong decoupling of P and Q that occurs in most high-voltage power systems.  His formulation is based upon the assumption that P is primarily related to 
[image: image85.wmf]d

, and that Q is primarily related to 
[image: image86.wmf]V

.

He begins by writing the expression for power at bus i, which is



[image: image87.wmf]*

1

,

ú

ú

û

ù

ê

ê

ë

é

=

+

å

=

N

j

j

j

i

i

calc

i

calc

i

V

y

V

jQ

P

 .

He then defines 



[image: image88.wmf]j

i

j

i

j

i

jB

G

y

,

,

,

+

=

 .

Expanding the power expression yields



[image: image89.wmf](

)

(

)

(

)

ú

ú

û

ù

ê

ê

ë

é

-

-

Ð

Ð

=

+

å

=

N

j

j

i

j

i

j

i

i

i

calc

i

calc

i

jB

G

V

V

jQ

P

1

,

,

q

q

,

or, expanding in real and imaginary form



[image: image90.wmf](

)

å

=

+

=

N

j

j

i

j

i

j

i

j

i

j

i

calc

i

B

G

V

V

P

1

,

,

,

,

sin

cos

d

d




[image: image91.wmf](

)

å

=

-

=

N

j

j

i

j

i

j

i

j

i

j

i

calc

i

B

G

V

V

Q

1

,

,

,

,

cos

sin

d

d

 ,

where 
[image: image92.wmf]j

i

j

i

d

d

d

-

=

,

 .

From the above equations, the necessary loadflow partial derivatives are



[image: image93.wmf](

)

j

i

j

i

j

i

j

i

j

i

i

j

j

i

B

G

V

V

P

,

,

,

,

cos

sin

d

d

¶d

¶

-

=

¹

 ,

and



[image: image94.wmf](

)

j

i

j

i

j

i

j

i

j

i

N

i

j

j

i

i

B

G

V

V

P

,

,

,

,

,

1

cos

sin

d

d

¶d

¶

+

-

=

å

¹

=

 ,

which, by comparing to the Q equation simplifies to



[image: image95.wmf](

)

ú

û

ù

ê

ë

é

-

-

-

=

i

i

j

i

i

i

i

i

i

i

i

i

B

G

V

Q

P

,

,

,

,

2

cos

sin

d

d

¶d

¶

 = 
[image: image96.wmf]i

i

i

i

B

V

Q

,

2

-

-

 .

Similarly, for Q,



[image: image97.wmf](

)

i

j

j

i

j

j

i

j

i

j

i

j

i

i

i

j

j

i

P

V

B

G

V

V

Q

¹

¹

=

-

=

¶d

¶

d

d

¶

¶

1

cos

sin

,

,

,

,

 ,

and



[image: image98.wmf](

)

(

)

i

i

i

i

i

i

i

i

i

N

i

j

j

j

i

j

i

j

i

j

i

j

i

i

B

G

V

B

G

V

V

Q

,

,

,

,

,

1

,

,

,

,

cos

sin

2

cos

sin

d

d

d

d

¶

¶

-

+

-

=

å

¹

=

 .

After simplifying, the above equation becomes



[image: image99.wmf]i

i

i

i

i

i

i

B

V

V

Q

V

Q

,

-

=

¶

¶

 .

The form of the Jacobian update equation is now



[image: image100.wmf]ú

ú

û

ù

ê

ê

ë

é

D

D

ú

û

ù

ê

ë

é

=

ú

û

ù

ê

ë

é

D

D

V

V

L

H

Q

P

1

0

0

d

 ,

where



[image: image101.wmf](

)

j

i

B

G

V

V

L

H

j

i

j

i

j

i

j

i

j

i

j

i

j

i

¹

-

=

=

 

,

cos

sin

,

,

,

,

,

,

d

d

 ,



[image: image102.wmf]i

i

i

i

i

i

B

V

Q

H

,

2

,

-

-

=

 ,



[image: image103.wmf]i

i

i

i

i

i

B

V

Q

L

,

2

,

-

=

 .

Now, since the angular differences are small, then 
[image: image104.wmf]j

i

j

i

,

,

sin

cos

d

d

>>

.  In reactive power systems, 
[image: image105.wmf]j

i

j

i

G

B

,

,

>

 , so that 
[image: image106.wmf]j

i

j

i

j

i

j

i

G

B

,

,

,

,

sin

cos

d

d

>>

 .  Also, in most cases, 
[image: image107.wmf]i

i

i

Q

B

>>

,

 , so that 
[image: image108.wmf]i

i

i

i

Q

B

V

>>

,

2

 .  Substituting these approximations into the above expressions for H and L yields



[image: image109.wmf]j

i

j

i

j

i

j

i

B

V

V

L

H

,

,

,

-

»

=

 ,



[image: image110.wmf]i

i

i

i

i

i

i

B

V

L

H

,

2

,

,

-

»

»

 .

These lead to the following simple form of the update equation:


[image: image111.wmf][

]

=

ú

ú

ú

ú

û

ù

ê

ê

ê

ê

ë

é

D

D

D

ú

ú

ú

ú

û

ù

ê

ê

ê

ê

ë

é

ú

ú

ú

ú

ú

û

ù

ê

ê

ê

ê

ê

ë

é

-

-

-

-

-

-

-

-

-

ú

ú

ú

ú

û

ù

ê

ê

ê

ê

ë

é

=

D

N

N

N

N

N

N

N

N

N

V

V

V

B

B

B

B

B

B

B

B

B

V

V

V

P

d

d

d

M

L

M

O

M

M

L

L

L

M

O

M

M

L

L

L

M

O

M

M

L

L

2

1

2

1

,

2

,

1

,

,

2

2

,

2

1

,

2

,

1

2

,

1

1

,

1

2

1

0

0

0

0

0

0

0

0

0

0

0

0



[image: image112.wmf][

]

d

D

=

V

VB

'

,


[image: image113.wmf][

]

=

ú

ú

ú

ú

ú

ú

ú

ú

û

ù

ê

ê

ê

ê

ê

ê

ê

ê

ë

é

D

D

D

ú

ú

ú

ú

û

ù

ê

ê

ê

ê

ë

é

ú

ú

ú

ú

ú

û

ù

ê

ê

ê

ê

ê

ë

é

-

-

-

-

-

-

-

-

-

ú

ú

ú

ú

û

ù

ê

ê

ê

ê

ë

é

=

D

N

N

N

N

N

N

N

N

N

N

V

V

V

V

V

V

V

V

V

B

B

B

B

B

B

B

B

B

V

V

V

Q

M

L

M

O

M

M

L

L

L

M

O

M

M

L

L

L

M

O

M

M

L

L

2

2

1

1

2

1

,

2

,

1

,

,

2

2

,

2

1

,

2

,

1

2

,

1

1

,

1

2

1

0

0

0

0

0

0

0

0

0

0

0

0



[image: image114.wmf]ú

û

ù

ê

ë

é

D

=

V

V

V

VB

'

'

.

Stott proposes the following additional simplifications:

1.
Omit from B' those network elements which primarily affect MVAr flows (i.e. shunt reactances, off-nominal transformer taps, etc.)

2.
Omit from B'' the angle-shifting effects of phase-shifting transformers, which primarily affect MW flows.

3.
Since the voltage magnitudes are close to unity, write




[image: image115.wmf][

]

[

]

[

]

[

]

d

d

D

»

D

=

ú

ú

û

ù

ê

ê

ë

é

D

 

 

'

'

B

V

B

V

P

 (first one-half iteration),


and




[image: image116.wmf][

]

[

]

[

]

V

B

V

V

V

B

V

Q

D

»

ú

ú

û

ù

ê

ê

ë

é

D

=

ú

ú

û

ù

ê

ê

ë

é

D

 

 

'

'

'

'

 (second one-half iteration).

4.
Neglect series resistances when calculating B'.

At this point, B' and B'' remain constant throughout the solution.  Therefore, B' and B'' should be LU decomposed once, and re-used for each half iteration.  The solutions steps are

1.
LU decompose B' and B''.

2.
Calculate 
[image: image117.wmf]ú

ú

û

ù

ê

ê

ë

é

D

V

P

 .

3.
Update 
[image: image118.wmf]d

 using 
[image: image119.wmf][

]

[

]

d

D

=

ú

ú

û

ù

ê

ê

ë

é

D

'

B

V

P

 .

4.
Check convergence, and continue if not converged.

5.
Calculate 
[image: image120.wmf]ú

ú

û

ù

ê

ê

ë

é

D

V

Q

 .

6.
Update 
[image: image121.wmf]V

D

 using 
[image: image122.wmf][

]

[

]

V

B

V

Q

D

=

ú

ú

û

ù

ê

ê

ë

é

D

'

'


7.
Check convergence, and return to Step 2 if not converged.

5.
Other Considerations

Current and Power Flow in Transmission Lines and Cables

Once the bus voltages throughout the system have been calculated, then the loadflow program must calculate power flows through lines/transformers/cables.  The standard pi-equivalent models are used for this purpose as follows:


[image: image123.wmf]R

jX

Icapj

Icapk

Ijk

Ikj

Vj/

d

j

Vk/

d

k

Q(pu)

2

Q(pu)

2

 ,

so from side j,

[image: image124.wmf](

)

0

90

2

+

Ð

+

+

Ð

-

Ð

=

j

j

k

k

j

j

jk

Q

V

jX

R

V

V

I

d

d

d

 ,

and from side k,

[image: image125.wmf](

)

0

90

2

+

Ð

+

+

Ð

-

Ð

=

k

k

j

j

k

k

kj

Q

V

jX

R

V

V

I

d

d

d

.

Note that the current on the two opposite ends of the line are not exactly the same due to the fact that the capacitor currents are not, in general, equal to each other.  The power flows for the two ends of the line, directed inward, are 
[image: image126.wmf]*

*

 

,

kj

kj

kj

jk

jk

jk

I

V

S

I

V

S

=

=

 .

Transmission line values for R, X (or L), and line charging Q (or C), shown on the previous diagram, are entered in per unit for the entire length of the line.  The relationship between these parameters and the per-meter calculations developed in the transmission line chapter follow.

· R and X = ωL are the positive-sequence per meter values of the transmission line (e.g., resistance of a phase bundle per meter, and ωL where L is approximately 1 mH per km), multiplied by the length of the transmission line, and converted to per unit ohms.

· C is the positive-sequence capacitance per meter of the transmission line, multiplied by the length of the transmission line.  Using C, then line charging Q is computed using base voltage with 
[image: image127.wmf]2

2

3

LL

LN

CV

CV

Q

w

w

=

=

.  Then, Q is converted to per unit, and half is placed on each end of the transmission line.  For a 345kV line at 60 Hz, and assuming 12 pF per meter, Q is about 0.538 MVAr per km.  The corresponding capacitive current to energize the line is then 0.90 A per km.

· One per unit Q corresponds to one per unit admittance Y.  It is standard practice in loadflows to represent Q/2 on each end of a line as an admittance jQ/2 (in per unit).  For the above example, and using a 100 MVA base, the line charging Q of a 100 km transmission would be 53.8 MVAr, and it would be modeled internally in the loadflow as admittances j0.269 pu mhos on each end.

Current and Power Flow in Transformers

The transformer equivalent circuit taken from Section 3 is


[image: image128.wmf]y

Ijk     

Ikj

Bus j

Bus k

q

t /

:1

Bus k'

Vj/

d

j

Vk/

d

k

,

so for side k,

[image: image129.wmf]y

t

V

V

I

j

j

k

k

kj

÷

÷

ø

ö

ç

ç

è

æ

Ð

Ð

-

Ð

=

q

d

d

,

and for side j,

[image: image130.wmf]q

Ð

-

=

t

I

I

kj

jk

 .

The corresponding power flows for the two ends of the transformer are 
[image: image131.wmf]*

*

 

,

kj

kj

kj

jk

jk

jk

I

V

S

I

V

S

=

=

 .

Area Interchange

Large-scale power systems usually consist of several, or perhaps many, individual electric utility companies.  In these cases, each area may have a desired net input or output power to satisfy sales and purchase agreements.

The area interchange feature in a loadflow program sums the tie-line flows into each area for a net area power input.  If these nets are not the desired values, to within a few megawatts, then an area-control generator within the area is adjusted by the error amount.  The sum of all input powers for all areas must, of course, be zero.

Convergence Criteria

Most loadflow data cases are developed using a 100 MVA base, so that a 1% load corresponds to 1 MW.  A typical convergence criteria is that the highest individual bus P and Q mismatches are within 0.001 - 0.01%, or 0.00001 - 0.0001 pu.

Page 1 of 16

_1209985828

_1209985966

_1209986059

_1209986114

_1209986199.unknown

_1209986323

_1209986325

_1425987097.unknown

_1427025299.unknown

_1209986324

_1209986319

_1209986321

_1209986322

_1209986320

_1209986315

_1209986317

_1209986318

_1209986316

_1209986233

_1209986236

_1209986314

_1209986210

_1209986135

_1209986168.unknown

_1209986188

_1209986138

_1209986121

_1209986125

_1209986117

_1209986084.unknown

_1209986100

_1209986107

_1209986110

_1209986104

_1209986094

_1209986097

_1209986091

_1209986072

_1209986078

_1209986081.unknown

_1209986074

_1209986064

_1209986069

_1209986062

_1209986011

_1209986036

_1209986049

_1209986055

_1209986045

_1209986024

_1209986029

_1209986014

_1209985980

_1209985996

_1209986002

_1209985991

_1209985974

_1209985977

_1209985971

_1209985896

_1209985936

_1209985953

_1209985960

_1209985963

_1209985957

_1209985946

_1209985950

_1209985942

_1209985924

_1209985930

_1209985933

_1209985927

_1209985911

_1209985916

_1209985904

_1209985858

_1209985876

_1209985882

_1209985888

_1209985879

_1209985869

_1209985873

_1209985861

_1209985846

_1209985853

_1209985856

_1209985850

_1209985840

_1209985843

_1209985836

_1209985756

_1209985787

_1209985803

_1209985812

_1209985822

_1209985808

_1209985793

_1209985800

_1209985790

_1209985771

_1209985780

_1209985783

_1209985775

_1209985762

_1209985768

_1209985758

_1209985710

_1209985733

_1209985747

_1209985750

_1209985737

_1209985725

_1209985728

_1209985722

_1209985685

_1209985692

_1209985699

_1209985688

_1209985670

_1209985678

_970752349

_1209985660

_963388596

