## Slide 1
3. Transformer Models.
Rs
jXs
Ideal
Transformer
7200:240V
Rm
jXm
7200V 240V
(approx. same amount of copper in each winding)
Turns ratio 7200:240
(30 : 1)
Φ

## Slide 2
3. Transformer Models, cont.
Open Circuit Test
Rs
jXs
Ideal
Transformer
7200:240V
Rm
jXm
7200V 240V
+
Voc
-
Open circuit test: Open circuit
the 7200V
-
side, and apply
240V to the 240V
-
side. The
winding currents are small, so
the series terms are negligible.
oc
oc
m
m
I
V
jX
R
~
~
||
=
Ioc
Turns ratio 7200:240
Φ

## Slide 3: Short Circuit Test
3. Transformer Models, cont.
Rs
jXs
Ideal
Transformer
7200:240V
Rm
jXm
7200V 240V
Turns ratio 7200:240
Φ
Short circuit test: Short circuit the 240V-side, and raise the 7200V-side voltage to a few percent of 7200, until rated current flows. There is almost no core flux so the magnetizing terms are negligible.
+
Vsc
-
Isc

## Slide 4
3. Transformer Models, cont.
Rs
jXs
Ideal
Transformer
Rm
jXm
X / R Ratios for Three
-
Phase Transformers
•
345kV to 138kV, X/R = 10
•
Substation transformers (e.g., 138kV to 25kV or 12.5kV, X/R = 2, X = 12%
•
25kV or 12.5kV to 480V, X/R = 1, X = 5%
•
480V class, X/R = 0.1, X = 1.5% to 4.5%

## Slide 5
3. Transformer Models, cont.
Single Phase Transformer. Percent values on transformer base.
Winding 1
kV = 7.2, kVA = 125
Winding 2
kV = 0.24, kVA = 125
%Imag = 0.5
%Load loss = 0.9
%No-load loss = 0.2
%Xs = 2.2
Rs
jXs
Ideal
Transformer
7200:240V
Rm
jXm
7200V 240V
Magnetizing current
No-load loss
Xs
Load loss
1. Given the standard percentage values below for a 125kVA transformer, determine the R’s and X’s in the diagram, in Ω.
If the R’s and X’s are moved to the 240V side, compute the new Ω values.
If standard open circuit and short circuit tests are performed on this transformer, what will be the P’s and Q’s (Watts and VArs) measured in those tests?

## Slide 6
3. Transformer Models, cont.
EPRI Study, Distribution Feeder Loss Example
•
Annual energy loss = 2.40%
•
Largest component is transformer no-load
loss (45% of the 2.40%)
Transformer No-
Load
45%
Transformer Load
8%
Primary Lines
26%
Secondary Lines
21%
Annual Feeder Loss Components
Modern Distribution Transformer:
Load loss at rated load (I2R in conductors) = 0.75% of rated transformer kW.
No load loss at rated voltage (magnetizing, core steel) = 0.2% of rated transformer kW.
Magnetizing current = 0.5% of rated transformer amperes

## Slide 7
3. Transformer Models, cont.
Y
-
Y
N1:N2
N1:N2
N1:N2
Rs
jXs
Ideal
Transformer
N1 : N2
Rm
jXm
Wye-Equivalent One-Line Model
A
N
•
Reflect to side 2 using individual transformer
turns ratio N1:N2
Standard 345/138kV autotransformers,
GY-GY
,
have a tertiary 12.5kV
Δ
winding to permit
circulating 3
rd
harmonic current
A three-phase transformer can be three separate single-phase transformers, or one large transformer with three sets of windings

## Slide 8
3. Transformer Models, cont.
Δ
-
Δ
N1:N2
N1:N2
N1:N2
Ideal
Transformer
3
Rs
3
2
:
3
1
N
N
3
jXs
3
Rm
3
jXm
A
N
•
Convert side 1 impedances from delta to
equivalent wye
•
Then reflect to side 2 using individual
transformer turns ratio N1:N2
For Modeling a Delta-Delta Connection, Convert the Transformer to Equivalent Wye-Wye
Wye-Equivalent One-Line Model

## Slide 9
3. Transformer Models, cont.
Δ
-
Y
N1:N2
N1:N2
N1:N2
Ideal
Transformer
3
Rs
2
:
3
1
N
N
3
jXs
3
Rm
3
jXm
A
N
For Modeling a Delta-Wye Connection, Convert the Transformer to Equivalent Wye-Wye
Wye-Equivalent One-Line Model
Convert side 1 impedances from delta to wye
Then reflect to side 2 using three-phase line-to-line turns ratio
Has 30° degree phase shift due to line-to-neutral to line-to-line relationship. ANSI standard requires the transformer to be labeled such that high-voltage side leads the low-voltage side by 30° .

## Slide 10
3. Transformer Models, cont.
Y
-
Δ
N1:N2
N1:N2
N1:N2
Ideal
Transformer
3
2
:
1
N
N
jXs
Rm
jXm
A
N
Rs
For Modeling a Wye-Delta Connection, Convert the Transformer to Equivalent Wye-Wye
Wye-Equivalent One-Line Model
Reflect to side 2 using three-phase bank line-to-line turns ratio
Has 30° degree phase shift due to line-to-neutral to line-to-line relationship. ANSI standard requires the transformer to be labeled such that high-voltage side leads the low-voltage side by 30°
Thus, for all configurations, equivalent wye-wye transformer ohms can be reflected from one side to the other using the three-phase bank line-to-line turns ratio